## NO Outage Cause Chart
Outages By Cause
ANIMAL | ANIMAL | 28 | 7.527%
CONDUCTOR | CONDUCTOR | 47 | 12.63%
EQUIPMENT | EQUIPMENT | 121 | 32.53%
HUMAN FACTORS | HUMAN FACTORS | 17 | 4.57%
LIGHTNING | LIGHTNING | 10 | 2.688%
OTHER | OTHER | 50 | 13.44%
OVERLOAD | OVERLOAD | 1 | 0.2688%
SCHEDULED INTERRUPTIONS | Scheduled Interruption | 57 | 15.32%
STORM | STORM | 0 | 0%
SUMMARY MISSING | Summary Missing | 19 | 5.108%
VEGETATION | VEGETATION | 22 | 5.914%
TOTAL OUTAGES |  | 372

## Outage Cause Category Details
SUMMARY_CAUSE | Cause Detail
ANIMAL | Animal - Squirrel | 24
| Animal - Raccoon | 2
| Animal - Other (Describe in Remarks Field) | 2
ANIMAL Total |  | 28
CONDUCTOR | Secondary/Service Conductor | 23
| Slack Conductor / Inadequate Phase Spacing | 3
| Equipment - Primary Conductor | 20
| Cable in duct | 1
CONDUCTOR Total |  | 47
EQUIPMENT | Equipment - Fuse Link | 17
| Equipment - Transformer | 36
| Equipment - Arrestor | 7
| Equipment - Pole | 11
| Equipment - Fuse Switch | 7
| Equipment - Crossarm | 18
| Equipment - Connector Sleeve | 13
| Equipment - Elbow | 2
| Equipment - Other (Describe in Remarks Field) | 4
| Equipment - Insulator | 6
EQUIPMENT Total |  | 121
HUMAN FACTORS | Human Error - Non-Entergy Workers (Describe in Remarks) | 3
| Vehicle | 9
| Contractor - Distribution Line (Describe in remarks) | 1
| Company - Distribution Line (Describe in remarks) | 4
HUMAN FACTORS Total |  | 17
LIGHTNING | Lightning | 10
LIGHTNING Total |  | 10
OTHER | Scheduled Interruption | 57
| Inspected Unknown | 19
| Foreign Objects - Other | 11
| Emergency Switching | 9
| Unknown - Under Investigation | 5
| Corrosion | 1
| Fire - Other (Describe in Remarks Field) | 1
| Mandated Outage per Public Authority (Describe in remarks) | 4
OTHER Total |  | 107
OVERLOAD | Overload | 1
OVERLOAD Total |  | 1
Summary Missing | Equipment - Connector / Sleeve | 19
Summary Missing Total |  | 19
VEGETATION | Overhanging Limb | 4
| Tree/Limb Growing Inside R.O.W. | 3
| Tree On Line Outside R.O.W. | 6
| Vine Growing into Line | 9
VEGETATION Total |  | 22
Grand Total |  | 372

## Outages by District & Weather
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
NAME | Weather Condition | SUMMARY_CAUSE | Cause Detail | Outage Date | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES1 | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 101
Council District B | [9 empty] | 63
Council District C | [9 empty] | 56
Council District D | [9 empty] | 78
Council District E | [9 empty] | 73
#N/A | [9 empty] | 1
Grand Total | [9 empty] | 372

## Outages by District & Zip Code
To view the Outage Details, click the box with the + symbol located to the left of the information you wish to view. As additional information becomes visible, click the box with + or - symbols to either expand or contract the desired information.
NAME | ZIP | SUMMARY_CAUSE | Cause Detail | Outage Date | LONGITUDE | LATITUDE | FEEDER_ID | TOTAL_DURATION_MINUTES1 | TOTAL_CUSTOMERS_AFFECTED | Total
Council District A | [9 empty] | 101
Council District B | [9 empty] | 63 | NOTE: Outages that occurred outside the physical boundaries of Algiers into Gretna are grouped into zip code 70056 – Council District C, as they are serviced by feeders from Algiers.
Council District C | [9 empty] | 56
Council District D | [9 empty] | 78
Council District E | [9 empty] | 73
#N/A | [9 empty] | 1
Grand Total | [9 empty] | 372

## Data
CASE_ID | In NOCC Reporting | NETWORK_NAME | WEATHER_CONDITION | FIRST_CALL_DATE_TIME | LAST_CALL_DATE_TIME | TROUBLE_CLEAR_TIME | FEEDER_ID | Feeder Owner | DEVICE_TYPE | DEVICE_ID | DISTRIBUTION_LOCATION_NBR | System_ | LOCAL_OFFICE_NBR | TOTAL_CUSTOMERS_AFFECTED | ACTUAL_CUSTOMER_MINUTES | TOTAL_DURATION_MINUTES1 | SUMMARY_CAUSE | CAUSE | CAUSE_DESC | MAJOR_EVENT | REMARKS | LONGITUDE | LATITUDE | ZIP | DISTRICTID | NAME | REPNAME
1300590647 | NO | ORLEANS | FAIR | 2018-12-03 09:55 | 2018-12-03 09:55 | 2018-12-03 11:28 | 2016 | ENOI | TFUS | SERVICE | 38249471828 | DLIN | 1 | 1 | 0 | 0 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 1554892 8 to ERR 1554892 [count]** --- CREW CASE, CREW WRKING POLE IN AREA, 1107, 12/3/18 rbeaco | -90.1255 | 29.9588 | 70118 | A | Council District A | Jay Banks
1300592810 | NO | ORLEANS | FAIR | 2018-12-03 11:40 | 2018-12-03 11:40 | 2018-12-03 13:03 | B0527 | ENOI | TFUS | SERVICE | 38093471229 | DLIN | 1 | 1 | 0 | 0 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 498854 18 to ERR 498854 [count]** --- crew outage three blks dwn, DOC DID NOT NOTIFY... 1107.. 12/3/18 rbeaco | -90.1305 | 29.9572 | 70118 | A | Council District A | Kristin Palmer
1301962732 | NO | ORLEANS | FAIR | 2019-01-02 11:39 | 2019-01-02 11:39 | 2019-01-02 13:58 | 512 | ENOI | XFMR | SERVICE | 39886491195 | DLIN | 1 | 1 | 0 | 0 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 26764 * 5 to ERR 26764 * [count]** --- CREW WORKING IN NEXT BLOCK, CREW SAID DOC WAS NOTIFIED, 1107, 1/2/19 rbeaco | -90.0732 | 30.0116 | 70122 | D | Council District D | Kristin Palmer
1302045506 | NO | ORLEANS | FAIR | 2019-01-05 13:54 | 2019-01-05 13:54 | 2019-01-05 14:22 | 2147 | ENOI | TFUS | SERVICE | 39633458845 | DLIN | 1 | 1 | 0 | 0 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 64298 19 to ERR 64298 19** --- crew working down street cschick | -90.0823 | 29.9228 | 70115 | B | Council District B | Joseph Giarrusso
1302219587 | Yes | EAST ORLEANS | FAIR | 2019-01-14 14:28 | 2019-01-14 14:28 | 2019-01-14 14:34 | 1601 | ENOI | TFUS | SERVICE | 44270501029 | DLIN | 6 | 1 | 6 | 6 | OTHER | SCHD | Scheduled Interruption | N | opened for repairs | -89.9343 | 30.0372 | 70129 | E | Council District E | Joseph Giarrusso
1302241418 | Yes | EAST ORLEANS | FAIR | 2019-01-15 13:44 | 2019-01-15 13:44 | 2019-01-15 13:51 | 2215 | ENOI | TFUS | SERVICE | 42546502278 | DLIN | 6 | 1 | 7 | 7 | OTHER | SCHD | Scheduled Interruption | N | reliability | -89.9886 | 30.0413 | 70127 | E | Council District E | Jared Brossett
1301390978 | Yes | ORLEANS | FAIR | 2018-12-20 09:17 | 2018-12-20 09:17 | 2018-12-20 09:40 | 1912 | ENOI | TFUS | 690851 | 38322456566 | DLIN | 1 | 1 | 23 | 23 | OTHER | SCHD | Scheduled Interruption | N | allen slamens had trans out for work. jar | -90.1237 | 29.9168 | 70118 | A | Council District A | Jay Banks
1302096980 | Yes | EAST ORLEANS | FAIR | 2019-01-08 14:10 | 2019-01-08 14:31 | 2019-01-08 14:41 | 502 | ENOI | TFUS | SERVICE | 40379490943 | DLIN | 6 | 1 | 31 | 31 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0575 | 30.0108 | 70122 | D | Council District D | Kristin Palmer
1300589743 | Yes | ORLEANS | FAIR | 2018-12-03 09:17 | 2018-12-03 09:17 | 2018-12-03 09:58 | 2015 | ENOI | TFUS | SERVICE | 38354468473 | DLIN | 1 | 1 | 41 | 41 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 67823 * 1 to SERV 67823 * 1** --- schedule maintaince, CREW ON SITE WORKING POLE.. 1107, 12/3/18 rbeaco | -90.1223 | 29.9496 | 70118 | A | Council District A | Kristin Palmer
1300618349 | Yes | ORLEANS | FAIR | 2018-12-04 12:57 | 2018-12-04 13:51 | 2018-12-04 13:51 | 1924 | ENOI | TFUS | SERVICE | 39145460756 | DLIN | 1 | 1 | 54 | 54 | OTHER | SCHD | Scheduled Interruption | N | crew transfering pole | -90.0975 | 29.9281 | 70115 | B | Council District B | Joseph Giarrusso
1302406497 | Yes | EAST ORLEANS | THDR | 2019-01-19 11:27 | 2019-01-19 11:27 | 2019-01-19 12:25 | 623 | ENOI | TFUS | SERVICE | 40491477140 | DLIN | 6 | 1 | 58 | 58 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0545 | 29.9727 | 70117 | C | Council District C | Joseph Giarrusso
1302700282 | Yes | ORLEANS | FAIR | 2019-01-27 08:12 | 2019-01-27 08:12 | 2019-01-27 09:11 | 2146 | ENOI | TFUS | SERVICE | 39588460574 | DLIN | 1 | 1 | 59 | 59 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0836 | 29.9275 | 70115 | B | Council District B | Cyndi Nguyen
1302138401 | Yes | ORLEANS | FAIR | 2019-01-10 04:19 | 2019-01-10 04:19 | 2019-01-10 05:25 | 614 | ENOI | TFUS | SERVICE | 40379475691 | DLIN | 1 | 1 | 66 | 66 | OTHER | SCHD | Scheduled Interruption | N | crew working at location | -90.0583 | 29.9688 | 70116 | C | Council District C | Kristin Palmer
1301164855 | Yes | ORLEANS | FAIR | 2018-12-17 10:15 | 2018-12-17 10:34 | 2018-12-17 11:27 | 2147 | ENOI | TFUS | 1032149 | 40052460972 | DLIN | 1 | 1 | 72 | 72 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.069 | 29.9284 | 70130 | B | Council District B | Jay Banks
1302552457 | Yes | ORLEANS | FAIR | 2019-01-22 11:29 | 2019-01-22 11:29 | 2019-01-22 12:46 | 2017 | ENOI | TFUS | SERVICE | 38570474746 | DLIN | 1 | 1 | 76 | 76 | OTHER | SCHD | Scheduled Interruption | N | UPGRADE TO SYSTEM..TRUCKS ARE ON SITE FOR SCHEDULED OUTAGE..ADVISED CUSTOMER OF OUTAGED djohn26 | -90.1154 | 29.9668 | 70118 | A | Council District A | Jay Banks
1302556637 | Yes | ORLEANS | FAIR | 2019-01-22 13:46 | 2019-01-22 13:46 | 2019-01-22 15:11 | 2017 | ENOI | TFUS | SERVICE | 38570474746 | DLIN | 1 | 1 | 85 | 85 | OTHER | SCHD | Scheduled Interruption | N | BUCKET TRUCKS STILL ON SITE PERFORMING UPGRADES... WILL HAVE POWER ON SHORTLY djohn26 | -90.1154 | 29.9668 | 70118 | A | Council District A | Joseph Giarrusso
1301438181 | Yes | EAST ORLEANS | FAIR | 2018-12-21 08:30 | 2018-12-21 08:30 | 2018-12-21 09:59 | 2215 | ENOI | TFUS | 62215 | 4289650449 | DLIN | 6 | 1 | 89 | 89 | OTHER | SCHD | Scheduled Interruption | N | CREW ON SITE | -89.9777 | 30.0472 | 70127 | E | Council District E | Joseph Giarrusso
1301440023 | Yes | EAST ORLEANS | FAIR | 2018-12-21 10:02 | 2018-12-21 10:02 | 2018-12-21 11:34 | 614 | ENOI | TFUS | 1304991 | 40452476855 | DLIN | 6 | 1 | 92 | 92 | OTHER | SCHD | Scheduled Interruption | N | CREW ON SITE | -90.0559 | 29.972 | 70117 | C | Council District C | Joseph Giarrusso
1300950817 | Yes | ORLEANS | FAIR | 2018-12-13 08:30 | 2018-12-13 08:30 | 2018-12-13 10:06 | 2132 | ENOI | TFUS | 1002569 | 39581465376 | DLIN | 1 | 1 | 96 | 96 | OTHER | SCHD | Scheduled Interruption | N | opened for safety of crew | -90.0836 | 29.9407 | 70113 | B | Council District B | Joseph Giarrusso
1302690459 | Yes | EAST ORLEANS | FAIR | 2019-01-26 10:15 | 2019-01-26 11:30 | 2019-01-26 11:55 | 1710 | ENOI | TFUS | SERVICE | 40424487365 | DLIN | 6 | 1 | 100 | 100 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0564 | 30.0009 | 70122 | D | Council District D | Jay Banks
1302140465 | Yes | ORLEANS | FAIR | 2019-01-10 08:26 | 2019-01-10 08:26 | 2019-01-10 10:27 | 1704 | ENOI | TFUS | SERVICE | 40276488291 | DLIN | 1 | 1 | 121 | 121 | OTHER | SCHD | Scheduled Interruption | N | bucket trucks on site working vemery SCHEDULED INTERUPTION | -90.0609 | 30.0035 | 70122 | D | Council District D | Jay Banks
1302295241 | Yes | EAST ORLEANS | FAIR | 2019-01-18 09:18 | 2019-01-18 11:05 | 2019-01-18 11:31 | 2347 | ENOI | TFUS | SERVICE | 41004474594 | DLIN | 6 | 1 | 132 | 132 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.0383 | 29.9656 | 70117 | C | Council District C | Jared Brossett
1301151854 | Yes | ORLEANS | FAIR | 2018-12-17 08:41 | 2018-12-17 08:41 | 2018-12-17 11:12 | 2132 | ENOI | TFUS | 1004992 | 39599464110 | DLIN | 1 | 1 | 151 | 151 | OTHER | SCHD | Scheduled Interruption | N | SCHEDULE OUTAGE, CONTRACTORS WORKING IN 1900, 2000 BLOCK... 1107, 12/17/18 rbeaco | -90.0832 | 29.9372 | 70113 | B | Council District B | Jay Banks
1300637696 | Yes | ORLEANS | FAIR | 2018-12-05 09:10 | 2018-12-05 10:03 | 2018-12-05 11:46 | 2146 | ENOI | TFUS | 1002567 | 39696458920 | DLIN | 1 | 1 | 156 | 156 | OTHER | SCHD | Scheduled Interruption | N | had to take out trans to change pole | -90.0802 | 29.923 | 70115 | B | Council District B | Joseph Giarrusso
1302812577 | Yes | ORLEANS | COLD | 2019-01-30 01:49 | 2019-01-30 02:12 | 2019-01-30 04:33 | 1913 | ENOI | TFUS | SERVICE | 38585458029 | DLIN | 1 | 1 | 164 | 164 | OTHER | SCHD | Scheduled Interruption | N | change rotten x arms | -90.1154 | 29.9209 | 70115 | A | Council District A | Jay Banks
1300950681 | Yes | ORLEANS | THDR | 2018-12-13 08:25 | 2018-12-13 11:10 | 2018-12-13 11:13 | 2021 | ENOI | TFUS | 33396 | 39547466578 | DLIN | 1 | 1 | 168 | 168 | OTHER | SCHD | Scheduled Interruption | N | contract crew on site | -90.0847 | 29.944 | 70113 | B | Council District B | Cyndi Nguyen
1300666067 | Yes | ORLEANS | FAIR | 2018-12-06 12:58 | 2018-12-06 12:58 | 2018-12-06 16:00 | 2013 | ENOI | TFUS | 79593 | 38292467523 | DLIN | 1 | 1 | 182 | 182 | OTHER | SCHD | Scheduled Interruption | N | crew outage | -90.1244 | 29.9469 | 70118 | A | Council District A | Joseph Giarrusso
1302138521 | Yes | ORLEANS | FAIR | 2019-01-10 05:09 | 2019-01-10 07:37 | 2019-01-10 08:33 | 614 | ENOI | LFUS | SERVICE | 4017847648 | DLIN | 1 | 1 | 204 | 204 | OTHER | SCHD | Scheduled Interruption | N | scheduled outage from 5-10 crew replacing cross arm | -90.0645 | 29.9709 | 70116 | C | Council District C | Joseph Giarrusso
1301071455 | Yes | ORLEANS | FAIR | 2018-12-16 09:18 | 2018-12-16 09:18 | 2018-12-16 12:54 | 2132 | ENOI | TFUS | 617925 | 3963846411 | DLIN | 1 | 1 | 215 | 215 | OTHER | SCHD | Scheduled Interruption | N | CREW ON SITE | -90.0819 | 29.9372 | 70113 | B | Council District B | Jay Banks
1300932671 | Yes | ALGIERS | FAIR | 2018-12-12 10:15 | 2018-12-12 12:18 | 2018-12-12 14:01 | W1712 | ENOI | LFUS | SERVICE | 4251345174 | DLIN | 81 | 1 | 226 | 226 | OTHER | SCHD | Scheduled Interruption | N | apartment complex needed outage to upgrade services | -89.9916 | 29.9023 | 70131 | C | Council District C | Jay Banks
1301072492 | Yes | ORLEANS | FAIR | 2018-12-16 09:33 | 2018-12-16 09:33 | 2018-12-16 13:20 | 2147 | ENOI | TFUS | 1130480 | 40052460972 | DLIN | 1 | 1 | 227 | 227 | OTHER | SCHD | Scheduled Interruption | N | CREW ON SITE SETTING POLE | -90.069 | 29.9284 | 70130 | B | Council District B | Joseph Giarrusso
1302064165 | Yes | ORLEANS | FAIR | 2019-01-07 09:02 | 2019-01-07 10:37 | 2019-01-07 13:01 | 2016 | ENOI | LFUS | SERVICE | 3839146759 | DLIN | 1 | 1 | 239 | 239 | OTHER | SCHD | Scheduled Interruption | N | crew to fix arm 337-207-0435 | -90.1213 | 29.9471 | 70118 | A | Council District A | Cyndi Nguyen
1301156462 | Yes | ORLEANS | FAIR | 2018-12-17 09:13 | 2018-12-17 11:10 | 2018-12-17 13:56 | 2147 | ENOI | TFUS | 29187 | 39481461270 | DLIN | 1 | 1 | 283 | 283 | OTHER | SCHD | Scheduled Interruption | N | contract crew on site | -90.0869 | 29.9295 | 70115 | B | Council District B | Joseph Giarrusso
1300658102 | Yes | ORLEANS | FAIR | 2018-12-06 07:45 | 2018-12-06 10:09 | 2018-12-06 14:00 | 2146 | ENOI | TFUS | 1401920 | 3975245866 | DLIN | 1 | 1 | 375 | 375 | OTHER | SCHD | Scheduled Interruption | N | opened to transfewr pole | -90.0785 | 29.9222 | 70130 | B | Council District B | Kristin Palmer
1302092628 | Yes | ORLEANS CBD | FAIR | 2019-01-08 11:23 | 2019-01-08 11:23 | 2019-01-08 17:57 | 1515 | ENOI | TFUS | SERVICE | 3959146941 | DLIN | 4 | 1 | 394 | 394 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0833 | 29.9518 | 70113 | B | Council District B | Joseph Giarrusso
1300660967 | Yes | ORLEANS | FAIR | 2018-12-06 09:24 | 2018-12-06 15:19 | 2018-12-06 16:00 | 2013 | ENOI | TFUS | 1403266 | 38307467388 | DLIN | 1 | 1 | 396 | 396 | OTHER | SCHD | Scheduled Interruption | N | 205 534 5076 | -90.1239 | 29.9465 | 70118 | A | Council District A | Jared Brossett
1300611777 | Yes | ORLEANS | FAIR | 2018-12-04 08:50 | 2018-12-04 14:08 | 2018-12-04 16:44 | 2022 | ENOI | TFUS | SERVICE | 38209472848 | DLIN | 1 | 1 | 474 | 474 | OTHER | SCHD | Scheduled Interruption | N |  | -90.1268 | 29.9617 | 70118 | A | Council District A | Jared Brossett
1302544743 | Yes | ORLEANS | FAIR | 2019-01-22 08:37 | 2019-01-22 16:34 | 2019-01-22 18:00 | 2026 | ENOI | DIS | SERVICE | 3852547424 | DLIN | 1 | 1 | 563 | 563 | OTHER | SCHD | Scheduled Interruption | N | scheduled outage to replace rotten crossarms | -90.1167 | 29.9654 | 70118 | A | Council District A | Jay Banks
1300594682 | NO | ORLEANS | FAIR | 2018-12-03 12:59 | 2018-12-03 13:00 | 2018-12-03 16:51 | 1924 | ENOI | TFUS | SERVICE | 39369461902 | DLIN | 1 | 2 | 0 | 0 | OTHER | SCHD | Scheduled Interruption | N | Changed **TFUS 63159 7 to ERR 63159 [count]** --- SCHEDULED OUTAGE, OH CREWS WRKING IN AREA, 1107, 12/3/18 rbeaco | -90.0904 | 29.9312 | 70115 | B | Council District B | Cyndi Nguyen
1300692393 | Yes | EAST ORLEANS | FAIR | 2018-12-07 11:33 | 2018-12-07 11:36 | 2018-12-07 12:11 | 2346 | ENOI | TFUS | 58730 | 41794471772 | DLIN | 6 | 2 | 76 | 38 | OTHER | SCHD | Scheduled Interruption | N | crew working at location | -90.0135 | 29.9576 | 70117 | E | Council District E | Joseph Giarrusso
1302262844 | Yes | ALGIERS | FAIR | 2019-01-16 13:51 | 2019-01-16 14:27 | 2019-01-16 14:41 | W1713 | ENOI | TFUS | SERVICE | 4203545699 | DLIN | 81 | 2 | 100 | 50 | OTHER | SCHD | Scheduled Interruption | N | crew work | -90.0065 | 29.9169 | 70131 | C | Council District C | Joseph Giarrusso
1302702951 | Yes | ALGIERS | FAIR | 2019-01-27 11:30 | 2019-01-27 11:59 | 2019-01-27 12:32 | W1726 | ENOI | TFUS | SERVICE | 4218045771 | DLIN | 81 | 2 | 124 | 62 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0019 | 29.9188 | 70131 | C | Council District C | Kristin Palmer
1302649668 | Yes | ORLEANS | FAIR | 2019-01-24 10:31 | 2019-01-24 10:48 | 2019-01-24 12:28 | 614 | ENOI | TFUS | SERVICE | 40406476041 | DLIN | 1 | 2 | 234 | 117 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.0572 | 29.9698 | 70116 | C | Council District C | Cyndi Nguyen
1300964543 | Yes | ORLEANS | RAIN | 2018-12-13 14:33 | 2018-12-13 15:02 | 2018-12-13 16:38 | 2012 | ENOI | TFUS | SERVICE | 39069479887 | DLIN | 1 | 2 | 250 | 125 | OTHER | SCHD | Scheduled Interruption | N | opened for safety to replace x arm | -90.0993 | 29.9807 | 70119 | A | Council District A | Cyndi Nguyen
1300937761 | Yes | ORLEANS | FAIR | 2018-12-12 13:42 | 2018-12-12 15:48 | 2018-12-12 16:47 | 2015 | ENOI | TFUS | SERVICE | 38336468354 | DLIN | 1 | 2 | 370 | 185 | OTHER | SCHD | Scheduled Interruption | N |  | -90.123 | 29.9493 | 70118 | A | Council District A | Joseph Giarrusso
1301155865 | Yes | ORLEANS | FAIR | 2018-12-17 09:08 | 2018-12-17 09:14 | 2018-12-17 13:01 | 1554 | ENOI | TFUS | 3006004 | 39279462893 | DLIN | 1 | 2 | 466 | 233 | OTHER | SCHD | Scheduled Interruption | N | crew on site | -90.0933 | 29.9339 | 70115 | B | Council District B | Cyndi Nguyen
1302699939 | Yes | ORLEANS | FAIR | 2019-01-27 07:06 | 2019-01-27 11:45 | 2019-01-27 13:00 | 2146 | ENOI | LFUS | SERVICE | 3953546136 | DLIN | 1 | 2 | 708 | 354 | OTHER | SCHD | Scheduled Interruption | N | crew working on feeder pole | -90.0852 | 29.9296 | 70115 | B | Council District B | Jared Brossett
1302699923 | Yes | ORLEANS | FAIR | 2019-01-27 07:05 | 2019-01-27 08:43 | 2019-01-27 13:00 | 2146 | ENOI | LFUS | SERVICE | 3953546136 | DLIN | 1 | 2 | 710 | 355 | OTHER | SCHD | Scheduled Interruption | N | crew working on feeder pole | -90.0851 | 29.9297 | 70115 | B | Council District B | Cyndi Nguyen
1300589025 | Yes | ORLEANS | FAIR | 2018-12-03 08:51 | 2018-12-03 11:02 | 2018-12-03 14:15 | 1922 | ENOI | LFUS | 27721 | 3942346295 | DLIN | 1 | 3 | 972 | 324 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0886 | 29.9341 | 70115 | B | Council District B | Cyndi Nguyen
1300992818 | Yes | ORLEANS | FAIR | 2018-12-14 09:04 | 2018-12-14 15:29 | 2018-12-14 15:32 | 2147 | ENOI | LFUS | 27799 | 3951546032 | DLIN | 1 | 4 | 1552 | 388 | OTHER | SCHD | Scheduled Interruption | N |  | -90.086 | 29.9267 | 70115 | B | Council District B | Jay Banks
1300635450 | Yes | ORLEANS | FAIR | 2018-12-05 08:30 | 2018-12-05 11:50 | 2018-12-05 15:00 | 2015 | ENOI | OPEN | 3835146855 | 3835146855 | DLIN | 1 | 5 | 1950 | 390 | OTHER | SCHD | Scheduled Interruption | N | Crew cutting in lateral switch at location | -90.1224 | 29.9498 | 70118 | A | Council District A | Jay Banks
1300944036 | Yes | ALGIERS | FAIR | 2018-12-12 20:14 | 2018-12-12 22:00 | 2018-12-12 23:00 | W1712 | ENOI | LFUS | 33314 | 4251345174 | DLIN | 81 | 8 | 1328 | 166 | OTHER | SCHD | Scheduled Interruption | N | crew opened dip to reconnect services (pwd) | -89.9916 | 29.9023 | 70131 | C | Council District C | Cyndi Nguyen
1302194807 | Yes | EAST ORLEANS | FAIR | 2019-01-13 08:56 | 2019-01-13 09:16 | 2019-01-13 09:26 | 623 | ENOI | LFUS | SERVICE | 4079547423 | DLIN | 6 | 9 | 270 | 30 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0451 | 29.9647 | 70117 | C | Council District C | Cyndi Nguyen
1302689437 | Yes | EAST ORLEANS | FAIR | 2019-01-26 09:00 | 2019-01-26 09:50 | 2019-01-26 10:05 | 1710 | ENOI | LFUS | SERVICE | 4042948691 | DLIN | 6 | 9 | 585 | 65 | OTHER | SCHD | Scheduled Interruption | N |  | -90.0563 | 29.9997 | 70122 | D | Council District D | Cyndi Nguyen
1300928412 | Yes | ORLEANS | FAIR | 2018-12-12 08:03 | 2018-12-12 08:37 | 2018-12-12 08:45 | 2015 | ENOI | LFUS | SERVICE | 3832946827 | DLIN | 1 | 12 | 504 | 42 | OTHER | SCHD | Scheduled Interruption | N | scheduled outage to repair pole | -90.1232 | 29.9491 | 70118 | A | Council District A | Jared Brossett
1300863935 | Yes | EAST ORLEANS | FAIR | 2018-12-10 09:04 | 2018-12-10 13:05 | 2018-12-10 13:00 | 1607 | ENOI | LFUS | 46249 | 4222549338 | DLIN | 6 | 17 | 4012 | 236 | OTHER | SCHD | Scheduled Interruption | N |  | -89.9991 | 30.0168 | 70126 | E | Council District E | Cyndi Nguyen
1300930673 | Yes | ORLEANS | FAIR | 2018-12-12 09:20 | 2018-12-12 17:24 | 2018-12-12 17:25 | 1554 | ENOI | DIS | SERVICE | 3934246340 | DLIN | 1 | 45 | 21825 | 485 | OTHER | SCHD | Scheduled Interruption | N | Crew on Site Working Chris Jones 601-446-8847 | -90.0912 | 29.9354 | 70115 | B | Council District B | Joseph Giarrusso
1301342322 | Yes | ORLEANS | RAIN | 2018-12-19 09:36 | 2018-12-19 09:36 | 2018-12-19 15:32 | 1923 | ENOI | TFUS | 61218 | 39026458924 | DLIN | 1 | 11 | 3916 | 356 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | found rat on trans. installed animal guard refused ok customer says she been out since saturday 12/15/18 been call ever since customer service told her we have trouble finding fuses whaaaaat jbologn | -90.1015 | 29.9231 | 70115 | B | Council District B | Cyndi Nguyen
1301783608 | Yes | ORLEANS | RAIN | 2018-12-28 10:50 | 2018-12-28 11:09 | 2018-12-28 11:40 | 1553 | ENOI | LFUS | 28044 | 3899447068 | DLIN | 1 | 12 | 600 | 50 | ANIMAL | AOTH | Animal - Other (Describe in Remarks Field) | N | found piegon on ground in front of 1224 s salcedo refused ok jbologn | -90.102 | 29.9554 | 70125 | B | Council District B | Joseph Giarrusso
1300932211 | Yes | EAST ORLEANS | FAIR | 2018-12-12 09:58 | 2018-12-12 10:05 | 2018-12-12 10:59 | 2346 | ENOI | LFUS | 31979 | 4208447715 | DLIN | 6 | 22 | 1342 | 61 | ANIMAL | ARAC | Animal - Raccoon | N | found raccoon on top of blown transformer in the 2300 blk of monticello which blew lateral 31979. removed raccoon from transformer and refused lateral. refused OK. checked mtrs. lit display dmorehe | -90.0042 | 29.9722 | 70117 | E | Council District E | Jared Brossett
1300575971 | Yes | ALGIERS | FAIR | 2018-12-02 11:48 | 2018-12-02 12:16 | 2018-12-02 12:38 | W1714 | ENOI | LFUS | 5591 | 4280645718 | DLIN | 81 | 31 | 1550 | 50 | ANIMAL | ARAC | Animal - Raccoon | N | refused ok zwashin | -89.9822 | 29.9171 | 70131 | C | Council District C | Jared Brossett
1300950515 | Yes | ALGIERS | FAIR | 2018-12-13 08:17 | 2018-12-13 08:17 | 2018-12-13 09:27 | W0712 | ENOI | TFUS | BY9-9901 | 4196045841 | DLIN | 81 | 4 | 280 | 70 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel caused outage gcharl1 | -90.0088 | 29.9208 | 70131 | C | Council District C | Jared Brossett
1301825120 | Yes | EAST ORLEANS | FAIR | 2018-12-30 14:45 | 2018-12-30 14:49 | 2018-12-30 16:04 | 2347 | ENOI | TFUS | 78652 | 41166473225 | DLIN | 6 | 4 | 316 | 79 | ANIMAL | ASQL | Animal - Squirrel | N | Refused transformer due to squirrel jvickna | -90.0334 | 29.9617 | 70117 | C | Council District C | Cyndi Nguyen
1301805077 | Yes | EAST ORLEANS | FAIR | 2018-12-29 09:04 | 2018-12-29 09:09 | 2018-12-29 10:38 | 2347 | ENOI | TFUS | 78652 | 41166473225 | DLIN | 6 | 4 | 376 | 94 | ANIMAL | ASQL | Animal - Squirrel | N | Refused transformer taken out by squirrel jvickna | -90.0334 | 29.9617 | 70117 | C | Council District C | Cyndi Nguyen
1302080461 | Yes | ORLEANS | FAIR | 2019-01-08 07:16 | 2019-01-08 08:04 | 2019-01-08 11:17 | 627 | ENOI | TFUS | 56801 | 40236479404 | DLIN | 1 | 4 | 964 | 241 | ANIMAL | ASQL | Animal - Squirrel | N | installed animal guard refused ok jbologn | -90.0625 | 29.9791 | 70119 | D | Council District D | Jared Brossett
1302543338 | Yes | ORLEANS | FAIR | 2019-01-22 07:45 | 2019-01-22 08:32 | 2019-01-22 09:08 | 510 | ENOI | TFUS | 33527 | 39797493121 | DLIN | 1 | 6 | 498 | 83 | ANIMAL | ASQL | Animal - Squirrel | N | installed animal guard refused ok jbologn | -90.0759 | 30.0168 | 70122 | D | Council District D | Cyndi Nguyen
1301456943 | Yes | ORLEANS | FAIR | 2018-12-22 07:17 | 2018-12-22 07:17 | 2018-12-22 09:10 | 408 | ENOI | TFUS | 19792 | 38746487117 | DLIN | 1 | 6 | 678 | 113 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel took out transformer refused ok rdeano | -90.1093 | 30.0007 | 70124 | A | Council District A | Cyndi Nguyen
1302053968 | Yes | ORLEANS | FAIR | 2019-01-06 08:31 | 2019-01-06 08:31 | 2019-01-06 10:09 | 2147 | ENOI | TFUS | 78536 | 39600457312 | DLIN | 1 | 7 | 686 | 98 | ANIMAL | ASQL | Animal - Squirrel | N | animal guarded and refused | -90.0833 | 29.919 | 70115 | B | Council District B | Cyndi Nguyen
1301742769 | Yes | ORLEANS | THDR | 2018-12-27 15:27 | 2018-12-27 15:28 | 2018-12-27 17:16 | 512 | ENOI | TFUS | 21971 | 39649492267 | DLIN | 1 | 7 | 763 | 109 | ANIMAL | ASQL | Animal - Squirrel | N | refused transforme taken out by squirrel | -90.0806 | 30.0147 | 70122 | D | Council District D | Kristin Palmer
1301130349 | Yes | ORLEANS | FAIR | 2018-12-17 06:50 | 2018-12-17 08:33 | 2018-12-17 09:16 | 406 | ENOI | TFUS | 19178 | 38959493158 | DLIN | 1 | 7 | 1022 | 146 | ANIMAL | ASQL | Animal - Squirrel | N | installed animal guard refused ok jbologn | -90.1024 | 30.0174 | 70124 | A | Council District A | Joseph Giarrusso
1300571247 | Yes | ORLEANS | FAIR | 2018-12-02 07:09 | 2018-12-02 08:23 | 2018-12-02 11:01 | 407 | ENOI | TFUS | 18065 | 38585484216 | DLIN | 1 | 7 | 1624 | 232 | ANIMAL | ASQL | Animal - Squirrel | N | refused ok with guard jruffi1 | -90.1146 | 29.9925 | 70124 | A | Council District A | Jay Banks
1300855141 | Yes | ORLEANS | COLD | 2018-12-10 07:06 | 2018-12-10 07:31 | 2018-12-10 08:15 | 2016 | ENOI | TFUS | 66889 | 38498468689 | DLIN | 1 | 8 | 552 | 69 | ANIMAL | ASQL | Animal - Squirrel | N | refused ok installed animal guard advised jbologn | -90.1178 | 29.9501 | 70118 | A | Council District A | Joseph Giarrusso
1302084445 | Yes | EAST ORLEANS | FAIR | 2019-01-08 09:31 | 2019-01-08 09:35 | 2019-01-08 10:46 | 1604 | ENOI | TFUS | 65677 | 42763494455 | DLIN | 6 | 8 | 600 | 75 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel took out transformer-cleared squirrel and re fused transformer-voltage ok-cust back on swalsh1 1-8-19 swalsh1 | -89.9822 | 30.0196 | 70127 | E | Council District E | Cyndi Nguyen
1302708096 | Yes | ORLEANS | FAIR | 2019-01-27 16:42 | 2019-01-27 17:19 | 2019-01-27 17:11 | 413 | ENOI | TFUS | 26423 | 38943485527 | DLIN | 1 | 9 | 261 | 29 | ANIMAL | ASQL | Animal - Squirrel | N | squirell got across top side of xfmr refused ok tsmit29 | -90.1031 | 29.9963 | 70124 | A | Council District A | Jay Banks
1301341650 | Yes | ORLEANS | FAIR | 2018-12-19 08:47 | 2018-12-19 08:47 | 2018-12-19 09:17 | 1911 | ENOI | TFUS | 64010 | 39524458831 | DLIN | 1 | 9 | 270 | 30 | ANIMAL | ASQL | Animal - Squirrel | N | installed animal guard refused ok advised jbologn | -90.0858 | 29.9227 | 70115 | B | Council District B | Kristin Palmer
1301511411 | Yes | ORLEANS | FAIR | 2018-12-25 07:34 | 2018-12-25 08:00 | 2018-12-25 09:38 | 408 | ENOI | TFUS | 26179 | 38781490953 | DLIN | 1 | 9 | 1116 | 124 | ANIMAL | ASQL | Animal - Squirrel | N | refused ok.per 310 treed3 | -90.108 | 30.0112 | 70124 | A | Council District A | Cyndi Nguyen
1302521170 | Yes | ALGIERS | FAIR | 2019-01-21 07:34 | 2019-01-21 08:07 | 2019-01-21 08:23 | W0722 | ENOI | TFUS | BY161287 | 4186346068 | DLIN | 81 | 14 | 686 | 49 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel got across transformer customer back in lights jthom15 | -90.0118 | 29.9271 | 70131 | C | Council District C | Joseph Giarrusso
1302836394 | Yes | ALGIERS | FAIR | 2019-01-31 10:01 | 2019-01-31 10:18 | 2019-01-31 10:42 | W0722 | ENOI | TFUS | 1590352 | 4195246279 | DLIN | 81 | 18 | 738 | 41 | ANIMAL | ASQL | Animal - Squirrel | N | squirrel found dead by pole, refused truffi1 | -90.0089 | 29.9329 | 70131 | C | Council District C | Kristin Palmer
1300572354 | Yes | ORLEANS | FAIR | 2018-12-02 08:22 | 2018-12-02 08:34 | 2018-12-02 10:22 | B0527 | ENOI | TFUS | 500753 | 38008464402 | DLIN | 1 | 18 | 2160 | 120 | ANIMAL | ASQL | Animal - Squirrel | N | refused ok replaced animal guard jruffi1 | -90.1334 | 29.9384 | 70118 | A | Council District A | Kristin Palmer
1300649748 | Yes | ALGIERS | FAIR | 2018-12-05 16:12 | 2018-12-05 16:19 | 2018-12-05 17:03 | W1725 | ENOI | TFUS | BY133022 | 4142546535 | DLIN | 81 | 20 | 1020 | 51 | ANIMAL | ASQL | Animal - Squirrel | N | back n now brizzut | -90.0254 | 29.9401 | 70114 | C | Council District C | Jay Banks
1302102590 | Yes | EAST ORLEANS | FAIR | 2019-01-08 18:05 | 2019-01-08 18:43 | 2019-01-08 19:16 | 1604 | ENOI | LFUS | 27887 | 4276849398 | DLIN | 6 | 22 | 1562 | 71 | ANIMAL | ASQL | Animal - Squirrel | N | refused c phase squreeel.. tbrock | -89.9821 | 30.0183 | 70127 | E | Council District E | Jay Banks
1301487327 | Yes | EAST ORLEANS | FAIR | 2018-12-23 16:10 | 2018-12-23 16:13 | 2018-12-23 17:51 | 1204 | ENOI | LFUS | 36302 | 48285511653 | DLIN | 6 | 30 | 3030 | 101 | ANIMAL | ASQL | Animal - Squirrel | N | b and c phase was blown from squirrel refused lateral 36302 and checked voltage need to come and remove old pots not being used and animal mitigate pole infront of 20844 chef hwy dwillin | -89.807 | 30.0651 | 70129 | E | Council District E | Cyndi Nguyen
1300864963 | Yes | ORLEANS | COLD | 2018-12-10 09:41 | 2018-12-10 10:14 | 2018-12-10 10:30 | 413 | ENOI | LFUS | 17547 | 3899748565 | DLIN | 1 | 40 | 1960 | 49 | ANIMAL | ASQL | Animal - Squirrel | N | found squirrel on top of xarm at brooks and argonne refused ok jbologn | -90.1014 | 29.9967 | 70124 | A | Council District A | Joseph Giarrusso
1301950114 | Yes | ORLEANS | FAIR | 2019-01-01 12:00 | 2019-01-01 12:09 | 2019-01-01 12:26 | 1924 | ENOI | LFUS | 21478 | 3908246060 | DLIN | 1 | 133 | 3458 | 26 | ANIMAL | ASQL | Animal - Squirrel | N | tfus was taken out by squirrel. cause lfus to blow as well. refused ok dsmit36 | -90.0997 | 29.9276 | 70115 | B | Council District B | Cyndi Nguyen
1301818232 | Yes | EAST ORLEANS | FOGG | 2018-12-30 07:56 | 2018-12-30 08:24 | 2018-12-30 09:34 | 1710 | ENOI | LFUS | 32033 | 4050548616 | DLIN | 6 | 244 | 23912 | 98 | ANIMAL | ASQL | Animal - Squirrel | N | Refused C phase at lateral sw# 32033 and refused transformer at 3908 Piedmont due to squirrel jvickna | -90.0537 | 29.9975 | 70122 | D | Council District D | Jay Banks
1300989554 | Yes | ORLEANS | FAIR | 2018-12-14 08:12 | 2018-12-14 08:41 | 2018-12-14 09:02 | 2021 | ENOI | LFUS | 37748 | 39624465843 | DLIN | 1 | 6 | 300 | 50 | OTHER | FOBJ | Foreign Objects - Other | N | piece of molding | -90.0824 | 29.9419 | 70113 | B | Council District B | Jay Banks
1301810039 | Yes | EAST ORLEANS | FAIR | 2018-12-29 13:55 | 2018-12-29 13:55 | 2018-12-29 15:20 | 1604 | ENOI | TFUS | 62486 | 42638493683 | DLIN | 6 | 7 | 595 | 85 | OTHER | FOBJ | Foreign Objects - Other | N | Refused transformer due to molding from pole ground causing fuse to blow jvickna | -89.9861 | 30.0175 | 70127 | E | Council District E | Joseph Giarrusso
1302752496 | Yes | EAST ORLEANS | FAIR | 2019-01-28 23:32 | 2019-01-28 23:40 | 2019-01-29 02:09 | 1710 | ENOI | TFUS | 59073 | 40536486988 | DLIN | 6 | 9 | 1413 | 157 | OTHER | FOBJ | Foreign Objects - Other | N | found dog toy thrown on top of transformer getting across high side bushings. refused ok. all cust back in lights. dwillin | -90.0528 | 29.9999 | 70122 | D | Council District D | Kristin Palmer
1301443452 | Yes | ORLEANS | COLD | 2018-12-21 10:52 | 2018-12-21 11:25 | 2018-12-21 12:30 | 407 | ENOI | TFUS | 21921 | 3861648402 | DLIN | 1 | 12 | 1176 | 98 | OTHER | FOBJ | Foreign Objects - Other | N | Changed **LFUS 21921 67 to TFUS 21921 67** --- transformer taken out by mylar balloon refused ok. per 310 treed3 | -90.1136 | 29.9922 | 70124 | A | Council District A | Kristin Palmer
1301809233 | Yes | ORLEANS | COLD | 2018-12-29 13:00 | 2018-12-29 13:06 | 2018-12-29 13:45 | 412 | ENOI | LFUS | 17777 | 3831448235 | DLIN | 1 | 26 | 1170 | 45 | OTHER | FOBJ | Foreign Objects - Other | N | balloons took out lfus. cleared balloons and refused dsmit36 | -90.123 | 29.9878 | 70124 | A | Council District A | Kristin Palmer
1302191072 | Yes | ORLEANS | COLD | 2019-01-13 03:01 | 2019-01-13 03:49 | 2019-01-13 04:50 | 615 | ENOI | LFUS | 77696 | 4010247716 | DLIN | 1 | 79 | 8611 | 109 | OTHER | FOBJ | Foreign Objects - Other | N | balloons took lfus out. refused ok dsmit36 | -90.0669 | 29.973 | 70116 | D | Council District D | Cyndi Nguyen
1300565003 | Yes | ORLEANS | FAIR | 2018-12-01 18:24 | 2018-12-01 19:51 | 2018-12-01 20:30 | 2027 | ENOI | LFUS | 27870 | 3869547162 | DLIN | 1 | 80 | 10080 | 126 | OTHER | FOBJ | Foreign Objects - Other | N | out due to the release of balloons. cleared and refused lateral dsmit36 | -90.1115 | 29.9581 | 70125 | B | Council District B | Jay Banks
1302202692 | Yes | EAST ORLEANS | FAIR | 2019-01-13 19:59 | 2019-01-13 20:33 | 2019-01-13 21:06 | 2215 | ENOI | LFUS | 27669 | 4245950386 | DLIN | 6 | 95 | 6365 | 67 | OTHER | FOBJ | Foreign Objects - Other | N | balloons | -89.9914 | 30.0457 | 70127 | E | Council District E | Jay Banks
1301426598 | Yes | ORLEANS | COLD | 2018-12-20 22:04 | 2018-12-20 22:40 | 2018-12-20 22:55 | 2012 | ENOI | LFUS | F24069 | 3887447985 | DLIN | 1 | 230 | 11730 | 51 | OTHER | FOBJ | Foreign Objects - Other | N | balloons took out lfus. removed and refused lateral dsmit36 | -90.1057 | 29.9807 | 70119 | A | Council District A | Jared Brossett
1301050883 | NO | EAST ORLEANS | FAIR | 2018-12-15 21:52 | 2018-12-15 21:52 | 2018-12-15 21:52 | 614 | ENOI | SBKR | 614 | 4081448420 | DLIN | 6 | 2338 | 0 | 0 | OTHER | FOBJ | Foreign Objects - Other | N | Crews found balloons contacted A phase of fdr 613 & apprent flashover took out fdr 614 @ Franklin & I-10/I-610 interchange on steell pole | -90.0441 | 29.9921 | 70126 | D | Council District D | Jared Brossett
1301050994 | Yes | EAST ORLEANS | FAIR | 2018-12-15 21:52 | 2018-12-16 00:32 | 2018-12-15 23:38 | 613 | ENOI | SBKR | 613 | 4081548420 | DLIN | 6 | 2635 | 279310 | 106 | OTHER | FOBJ | Foreign Objects - Other | N | Crews found balloons contacted A phase of fdr. 613 & apparent flashover took out fdr 614 @ Franklin & I-10/I-610 interchange steel pole | -90.0441 | 29.9921 | 70126 | D | Council District D | Jared Brossett
1302098964 | Yes | EAST ORLEANS | FAIR | 2019-01-08 15:02 | 2019-01-08 15:33 | 2019-01-08 16:06 | 2212 | ENOI | LFUS | 24311 | 4173149985 | DLIN | 6 | 11 | 704 | 64 | HUMAN FACTORS | HNWK | Human Error - Non-Entergy Workers (Describe in Remarks) | N | S&WB dug into line on Exeter st by Curran Blvd | -90.0146 | 30.0348 | 70126 | E | Council District E | Jared Brossett
1302148092 | Yes | EAST ORLEANS | FAIR | 2019-01-10 11:56 | 2019-01-10 11:56 | 2019-01-10 17:27 | 1205 | ENOI | TFUS | 1294808 | 44647502567 | DLIN | 6 | 16 | 5296 | 331 | HUMAN FACTORS | HNWK | Human Error - Non-Entergy Workers (Describe in Remarks) | N | REPAIR CABLE THAT WAS DUG INTO | -89.9223 | 30.0413 | 70129 | E | Council District E | Jared Brossett
1302066281 | Yes | ALGIERS | FAIR | 2019-01-07 10:41 | 2019-01-07 11:33 | 2019-01-07 11:34 | W0715 | ENOI | RCLR | 37215 | 4110146257 | DLIN | 81 | 932 | 49396 | 53 | HUMAN FACTORS | HNWK | Human Error - Non-Entergy Workers (Describe in Remarks) | N | worker for sprint got bucket truck into feeder taking out recloser 37215 | -90.0358 | 29.9325 | 70114 | C | Council District C | Jay Banks
1300514671 | Yes | ORLEANS | THDR | 2018-12-01 02:22 | 2018-12-01 02:22 | 2018-12-01 03:34 | 614 | ENOI | TFUS | 1 | 4030147718 | DLIN | 1 | 1 | 72 | 72 | LIGHTNING | LGHT | Lightning | N | out by weather. refused ok dsmit36 | -90.0606 | 29.973 | 70116 | C | Council District C | Jay Banks
1301833023 | Yes | EAST ORLEANS | THDR | 2018-12-31 04:37 | 2018-12-31 04:37 | 2018-12-31 06:33 | 1604 | ENOI | TFUS | 68339 | 42649492651 | DLIN | 6 | 2 | 232 | 116 | LIGHTNING | LGHT | Lightning | N | weather | -89.9858 | 30.0147 | 70127 | E | Council District E | Joseph Giarrusso
1300514508 | Yes | ORLEANS | THDR | 2018-12-01 02:13 | 2018-12-01 02:13 | 2018-12-01 03:34 | 614 | ENOI | TFUS | 58911 | 40181477094 | DLIN | 1 | 4 | 324 | 81 | LIGHTNING | LGHT | Lightning | N | out by weather. refused ok dsmit36 | -90.0644 | 29.9728 | 70116 | C | Council District C | Joseph Giarrusso
1300507057 | Yes | ORLEANS | THDR | 2018-12-01 00:37 | 2018-12-01 00:56 | 2018-12-01 01:50 | 1925 | ENOI | TFUS | 61372 | 39090463305 | DLIN | 1 | 7 | 511 | 73 | LIGHTNING | LGHT | Lightning | N | bad weather. refused ok dsmit36 | -90.0993 | 29.9351 | 70115 | B | Council District B | Jay Banks
1301359648 | Yes | ORLEANS | THDR | 2018-12-19 13:15 | 2018-12-19 13:15 | 2018-12-19 15:31 | 911 | ENOI | TFUS | 59717 | 39688474204 | DLIN | 1 | 9 | 1224 | 136 | LIGHTNING | LGHT | Lightning | N | 29 OTHER/MISCELLANEOUS send to bucket...no power coming in..looks like blown fuse. djohn26 | -90.0799 | 29.9649 | 70119 | B | Council District B | Cyndi Nguyen
1301387322 | Yes | ORLEANS | COLD | 2018-12-19 21:26 | 2018-12-19 21:33 | 2018-12-19 21:59 | 2021 | ENOI | TFUS | 62326 | 39095468031 | DLIN | 1 | 25 | 825 | 33 | LIGHTNING | LGHT | Lightning | N | tfus went out earlier in the day with bad weaher. refused ok dsmit36 | -90.0989 | 29.9482 | 70125 | B | Council District B | Jay Banks
1301981024 | Yes | ORLEANS | FAIR | 2019-01-03 02:06 | 2019-01-03 02:49 | 2019-01-03 03:31 | 1709 | ENOI | LFUS | 37782 | 3986548109 | DLIN | 1 | 63 | 5355 | 85 | LIGHTNING | LGHT | Lightning | N |  | -90.0743 | 29.9838 | 70119 | D | Council District D | Jay Banks
1301743824 | Yes | ORLEANS | THDR | 2018-12-27 15:40 | 2018-12-27 15:56 | 2018-12-27 16:51 | 904 | ENOI | LFUS | 21540 | 3928247956 | DLIN | 1 | 96 | 6816 | 71 | LIGHTNING | LGHT | Lightning | N | crew refused laterial | -90.0927 | 29.9798 | 70119 | A | Council District A | Jay Banks
1301832949 | Yes | EAST ORLEANS | WIND | 2018-12-31 04:31 | 2018-12-31 06:31 | 2018-12-31 06:33 | 1604 | ENOI | RCLR | 24864 | 4288049405 | DLIN | 6 | 726 | 88572 | 122 | LIGHTNING | LGHT | Lightning | N | weather/recloser 24804 closed and held | -89.9785 | 30.0186 | 70127 | E | Council District E | Kristin Palmer
1301804057 | NO | ORLEANS | RAIN | 2018-12-29 07:04 | 2018-12-29 07:04 | 2018-12-29 07:04 | 1705 | ENOI | SBKR | 1705 | 4023648723 | DLIN | 1 | 2212 | 0 | 0 | LIGHTNING | LGHT | Lightning | N | weather | -90.0623 | 30.0006 | 70122 | D | Council District D | Cyndi Nguyen
1300645831 | NO | ORLEANS | FAIR | 2018-12-05 14:00 | 2018-12-05 14:02 | 2018-12-05 17:24 | 2026 | ENOI | TFUS | 68051 | 38660477549 | DLIN | 1 | 6 | 1224 | 204 | OTHER | MNDT | Mandated Outage per Public Authority (Describe in remarks) | N | out due to early morning fire. refused ok per 310 treed3 | -90.1117 | 29.9748 | 70118 | A | Council District A | Jay Banks
1300644324 | NO | ORLEANS | FAIR | 2018-12-05 13:01 | 2018-12-05 16:16 | 2018-12-05 17:22 | 2026 | ENOI | TFUS | 68438 | 38678477387 | DLIN | 1 | 8 | 2088 | 261 | OTHER | MNDT | Mandated Outage per Public Authority (Describe in remarks) | N | out due to early morning fire. refused ok per 310 treed3 | -90.1118 | 29.9741 | 70118 | A | Council District A | Jay Banks
1302009961 | NO | ORLEANS | FAIR | 2019-01-03 21:27 | 2019-01-03 23:39 | 2019-01-04 01:11 | 2132 | ENOI | TFUS | 1005294 | 39757460363 | DLIN | 1 | 10 | 2240 | 224 | OTHER | MNDT | Mandated Outage per Public Authority (Describe in remarks) | N | had to drop out for fire dept | -90.0784 | 29.9268 | 70130 | B | Council District B | Joseph Giarrusso
1300630307 | NO | ORLEANS | FAIR | 2018-12-05 04:55 | 2018-12-05 05:01 | 2018-12-05 05:15 | 2026 | ENOI | LFUS | 86912 | 3864947718 | DLIN | 1 | 24 | 456 | 19 | OTHER | MNDT | Mandated Outage per Public Authority (Describe in remarks) | N | structure fire had to drop lateral | -90.1127 | 29.9735 | 70118 | A | Council District A | Cyndi Nguyen
1301439096 | Yes | ORLEANS | COLD | 2018-12-21 09:17 | 2018-12-21 09:17 | 2018-12-21 10:30 | 2012 | ENOI | TFUS | 66833 | 39153482579 | DLIN | 1 | 2 | 146 | 73 | VEGETATION | VOHL | Overhanging Limb | N | cleared tree limb refused ok. per 310 treed3 | -90.0966 | 29.9881 | 70124 | A | Council District A | Jay Banks
1300937581 | Yes | EAST ORLEANS | FAIR | 2018-12-12 13:32 | 2018-12-12 13:32 | 2018-12-12 18:16 | 1204 | ENOI | TFUS | 3004831 | 49659531399 | DLIN | 6 | 4 | 1136 | 284 | VEGETATION | VOHL | Overhanging Limb | N | crew to repair hot leg in tree | -89.7629 | 30.1189 | 70129 | E | Council District E | Jay Banks
1301935464 | Yes | ORLEANS | FOGG | 2019-01-01 | 2019-01-01 01:32 | 2019-01-01 01:32 | 400 | ENOI | SBKR | 400 | 3847049127 | DLIN | 1 | 29 | 2668 | 92 | VEGETATION | VOHL | Overhanging Limb | N | opened at TP pole 14256 feeder held still riding out past this open switch: See Switch case | -90.1179 | 30.0122 | 70124 | A | Council District A | Jay Banks
1301936325 | Yes | ORLEANS | FOGG | 2019-01-01 | 2019-01-01 02:13 | 2019-01-01 02:48 | 400 | ENOI | DIS | 14256 | 3832948491 | DLIN | 1 | 280 | 47040 | 168 | VEGETATION | VOHL | Overhanging Limb | N | tree fell across sheild and primary cut in clear | -90.1226 | 29.9949 | 70124 | A | Council District A | Jay Banks
1302623580 | Yes | ALGIERS | RAIN | 2019-01-23 13:04 | 2019-01-23 13:04 | 2019-01-23 13:28 | W0115 | ENOI | SERV | SERVICE | 4075146417 | DLIN | 81 | 1 | 23 | 23 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | Changed **TFUS BY161451 13 to SERV BY161451 1** --- customer needs temp disco to cut tree so we can raise service nwashi1 | -90.0468 | 29.937 | 70114 | C | Council District C | Jared Brossett
1300545157 | Yes | EAST ORLEANS | FAIR | 2018-12-01 11:26 | 2018-12-01 11:26 | 2018-12-01 13:09 | 1710 | ENOI | SERV | 1428782 | 40428487298 | DLIN | 6 | 1 | 103 | 103 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | made repaires in tree cscale1 | -90.0562 | 30.0007 | 70122 | D | Council District D | Joseph Giarrusso
1301572073 | Yes | EAST ORLEANS | THDR | 2018-12-26 22:02 | 2018-12-26 22:10 | 2018-12-26 22:21 | 502 | ENOI | LFUS | 89454 | 40444491532 | DLIN | 6 | 12 | 228 | 19 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | tree | -90.0556 | 30.0122 | 70122 | D | Council District D | Kristin Palmer
1302459235 | Yes | ALGIERS | WIND | 2019-01-19 17:20 | 2019-01-19 17:34 | 2019-01-19 20:30 | W1726 | ENOI | TFUS | BY122690 | 4272745896 | DLIN | 81 | 15 | 2850 | 190 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | tree fell took out service back up brizzut | -89.9846 | 29.9221 | 70131 | C | Council District C | Kristin Palmer
1302007851 | Yes | ORLEANS | THDR | 2019-01-03 18:28 | 2019-01-03 22:14 | 2019-01-04 03:24 | 1926 | ENOI | OPEN | 3858446250 | 3858446250 | DLIN | 1 | 281 | 77686 | 536 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N |  | -90.1153 | 29.9331 | 70115 | A | Council District A | Joseph Giarrusso
1301975834 | NO | ORLEANS | FAIR | 2019-01-02 20:29 | 2019-01-02 20:30 | 2019-01-02 20:29 | 1704 | ENOI | SBKR | 1704 | 4023848723 | DLIN | 1 | 3115 | 0 | 0 | VEGETATION | VLFL | Tree On Line Outside R.O.W. | N | **NO FOLLOW-UP NEEDED PER OC** | -90.0622 | 30.0006 | 70122 | D | Council District D | Joseph Giarrusso
1301612740 | Yes | ORLEANS | THDR | 2018-12-27 02:52 | 2018-12-27 02:53 | 2018-12-27 05:51 | 1922 | ENOI | TFUS | 59448 | 39256457455 | DLIN | 1 | 13 | 2327 | 179 | VEGETATION | VLGL | Tree/Limb Growing Inside R.O.W. | N | cust palm tree took out xfmr repaced barrel tsmit29 | -90.0943 | 29.919 | 70115 | B | Council District B | Jared Brossett
1302021407 | Yes | ORLEANS | THDR | 2019-01-04 06:34 | 2019-01-04 07:29 | 2019-01-04 07:36 | 1917 | ENOI | LFUS | 21083 | 3852946097 | DLIN | 1 | 18 | 1116 | 62 | VEGETATION | VLGL | Tree/Limb Growing Inside R.O.W. | N | cleared limb off line in 1500 blk nashville refused ok been out since last night when weather came through per customer jbologn | -90.117 | 29.9288 | 70115 | A | Council District A | Jared Brossett
1302480302 | Yes | ALGIERS | WIND | 2019-01-19 20:26 | 2019-01-19 20:46 | 2019-01-19 21:25 | W0723 | ENOI | LFUS | 11513 | 4166746482 | DLIN | 81 | 21 | 1239 | 59 | VEGETATION | VLGL | Tree/Limb Growing Inside R.O.W. | N | branch on primary removed lat back n now brizzut | -90.0179 | 29.9385 | 70114 | C | Council District C | Jared Brossett
1300681912 | Yes | ORLEANS | FAIR | 2018-12-06 22:25 | 2018-12-06 22:25 | 2018-12-06 22:51 | 2022 | ENOI | SERV | SERVICE | 38253473855 | DLIN | 1 | 1 | 26 | 26 | HUMAN FACTORS | VHCL | Vehicle | N | Changed **TFUS 1400852 11 to SERV 1400852 1** --- customer stated a truck pulled down the service. reconnected service to house ok. per 310 treed3 minimal cla | -90.1254 | 29.9644 | 70118 | A | Council District A | Cyndi Nguyen
1302228083 | Yes | EAST ORLEANS | FAIR | 2019-01-14 20:40 | 2019-01-14 20:40 | 2019-01-15 02:18 | 2346 | ENOI | TFUS | 58577 | 41584473407 | DLIN | 6 | 5 | 1690 | 338 | HUMAN FACTORS | VHCL | Vehicle | N | Crew changing broken pole at location...complete | -90.0202 | 29.9621 | 70117 | E | Council District E | Joseph Giarrusso
1300581264 | Yes | ORLEANS | FAIR | 2018-12-02 17:28 | 2018-12-02 17:47 | 2018-12-02 20:55 | 2147 | ENOI | TFUS | 63907 | 39560458836 | DLIN | 1 | 6 | 1242 | 207 | HUMAN FACTORS | VHCL | Vehicle | N | crew repaired broken wilson rack pulled down by truck that caught service line ***ADDED TO MINIMAL CLAIMS LIST*** | -90.0845 | 29.9226 | 70115 | B | Council District B | Jared Brossett
1302702897 | Yes | ORLEANS | FAIR | 2019-01-27 11:28 | 2019-01-27 11:28 | 2019-01-27 11:41 | 411 | ENOI | TFUS | 1034091 | 38790491810 | DLIN | 1 | 8 | 104 | 13 | HUMAN FACTORS | VHCL | Vehicle | N | when car hit pole it caused lateral to blow one phase refused ok no car here for information for 123 form crew coming to change pole tsmit29 *CLAIMS 01/28/19** | -90.1077 | 30.0136 | 70124 | A | Council District A | Cyndi Nguyen
1301478355 | Yes | ORLEANS | FAIR | 2018-12-23 07:22 | 2018-12-23 08:04 | 2018-12-23 08:29 | 2011 | ENOI | SBKR | 2011 | 3847347393 | DLIN | 1 | 31 | 2077 | 67 | HUMAN FACTORS | VHCL | Vehicle | N | Car hit pole knocking wire down, crew enroute to pick up wire. Feeder has been closed ***SENT PID FORM TO CLAIMS *** | -90.1184 | 29.9645 | 70118 | A | Council District A | Joseph Giarrusso
1302325607 | Yes | EAST ORLEANS | FAIR | 2019-01-19 01:21 | 2019-01-19 07:02 | 2019-01-19 07:00 | 622 | ENOI | LFUS | 27850 | 4092947726 | DLIN | 6 | 159 | 53901 | 339 | HUMAN FACTORS | VHCL | Vehicle | N | car hit pole | -90.0408 | 29.973 | 70117 | D | Council District D | Jared Brossett
1301526353 | Yes | ALGIERS | FAIR | 2018-12-26 13:21 | 2018-12-26 15:09 | 2018-12-26 16:30 | W0725 | ENOI | RCLR | 5123 | 4150446191 | DLIN | 81 | 162 | 30618 | 189 | HUMAN FACTORS | VHCL | Vehicle | N | 18wheeler broker 30 pole, 2 cross arms and burned down primary. Crew on site | -90.0231 | 29.9306 | 70114 | C | Council District C | Jared Brossett
1301036330 | Yes | ALGIERS | COLD | 2018-12-15 02:34 | 2018-12-15 11:20 | 2018-12-15 11:23 | W1714 | ENOI | DIS | 5166 | 4245645453 | DLIN | 81 | 227 | 120083 | 529 | HUMAN FACTORS | VHCL | Vehicle | N | broke pole DUP TICKET# 1301034838, 1301035168, 1301035624 (AKS) | -89.9934 | 29.91 | 70131 | C | Council District C | Kristin Palmer
1301034838 | NO | ALGIERS | FAIR | 2018-12-15 02:12 | 2018-12-15 02:12 | 2018-12-15 02:13 | W1714 | ENOI | SBKR | W1714 | 4283945922 | DLIN | 81 | 1751 | 3502 | 2 | HUMAN FACTORS | VHCL | Vehicle | N | car hit pole DUPLICATE TICKET# 1301035168, 1301036330, 1301035624 (AKS) | -89.9811 | 29.9228 | 70131 | C | Council District C | Joseph Giarrusso
1302063350 | Yes | ORLEANS | FAIR | 2019-01-07 08:11 | 2019-01-07 08:11 | 2019-01-07 09:17 | 1917 | ENOI | TFUS | 489554 | 3845545694 | DLIN | 1 | 1 | 66 | 66 | VEGETATION | VINE | Vine Growing into Line | N | cleared vine from riser. refused ok. per 310 treed3 | -90.1195 | 29.9178 | 70115 | A | Council District A | Jay Banks
1302512724 | Yes | ORLEANS | COLD | 2019-01-20 18:08 | 2019-01-20 18:08 | 2019-01-20 20:21 | 2137 | ENOI | TFUS | 1562551 | 39942464561 | DLIN | 1 | 4 | 532 | 133 | VEGETATION | VINE | Vine Growing into Line | N | vines growing on transformer, cut vines and refused lighting pot jcox7 | -90.0723 | 29.9384 | 70130 | B | Council District B | Kristin Palmer
1301619071 | Yes | ORLEANS | WIND | 2018-12-27 03:54 | 2018-12-27 08:38 | 2018-12-27 09:06 | 1709 | ENOI | TFUS | 54952 | 40010480875 | DLIN | 1 | 8 | 2496 | 312 | VEGETATION | VINE | Vine Growing into Line | N | refused transformer ok outage caused by vines to bare riser changed riser to insulated an animal guarded ok advised customer about vines jdomang | -90.0696 | 29.9831 | 70119 | D | Council District D | Joseph Giarrusso
1301758441 | NO | ORLEANS | WIND | 2018-12-27 18:12 | 2018-12-27 18:44 | 2018-12-27 18:16 | 904 | ENOI | TFUS | 1205935 | 39387479600 | DLIN | 1 | 13 | 52 | 4 | VEGETATION | VINE | Vine Growing into Line | N | cleared vines off of xfmr refused tsmit29 | -90.0894 | 29.9799 | 70119 | A | Council District A | Cyndi Nguyen
1301513941 | Yes | ALGIERS | FAIR | 2018-12-25 11:21 | 2018-12-25 11:27 | 2018-12-25 12:50 | W1714 | ENOI | TFUS | 1205799 | 4280345686 | DLIN | 81 | 16 | 1424 | 89 | VEGETATION | VINE | Vine Growing into Line | N | Vines on pole took out transformer | -89.9823 | 29.9163 | 70131 | C | Council District C | Joseph Giarrusso
1301383490 | Yes | ORLEANS | RAIN | 2018-12-19 14:37 | 2018-12-19 16:14 | 2018-12-19 16:15 | 2017 | ENOI | LFUS | F05720 | 3894747329 | DLIN | 1 | 47 | 4606 | 98 | VEGETATION | VINE | Vine Growing into Line | N | refused C phase cleared vines on pole jbologn | -90.1035 | 29.9627 | 70125 | B | Council District B | Cyndi Nguyen
1300785378 | Yes | ORLEANS | RAIN | 2018-12-08 21:45 | 2018-12-08 22:55 | 2018-12-08 23:18 | 1922 | ENOI | LFUS | 56372 | 39098467163 | DLIN | 1 | 50 | 4650 | 93 | VEGETATION | VINE | Vine Growing into Line | N | cleared vines and bad aerrestor. per 310 refused ok treed3 | -90.0988 | 29.9457 | 70125 | B | Council District B | Joseph Giarrusso
1300768453 | Yes | ORLEANS | RAIN | 2018-12-08 18:19 | 2018-12-08 21:02 | 2018-12-08 21:07 | 1922 | ENOI | LFUS | 27675 | 3910546720 | DLIN | 1 | 95 | 15960 | 168 | VEGETATION | VINE | Vine Growing into Line | N | Changed **LFUS 27675 104 to LFUS 27675 95** --- refused ok. treed3 | -90.0987 | 29.9458 | 70125 | B | Council District B | Kristin Palmer
1301849174 | Yes | ORLEANS | THDR | 2018-12-31 06:31 | 2018-12-31 07:01 | 2018-12-31 07:28 | 2016 | ENOI | LFUS | 33243 | 3832347263 | DLIN | 1 | 144 | 8208 | 57 | VEGETATION | VINE | Vine Growing into Line | N | Changed **LFUS 33243 175 to LFUS 33243 141** --- refused B phase cleared vines on pole at apple and eagle jbologn | -90.1232 | 29.9609 | 70118 | A | Council District A | Joseph Giarrusso
1301500995 | Yes | ORLEANS | FAIR | 2018-12-24 17:47 | 2018-12-24 22:39 | 2018-12-24 19:01 | 406 | ENOI | LFUS | 17685 | 3907149369 | DLIN | 1 | 290 | 21460 | 74 | CONDUCTOR | CFID | Cable in duct | N | Changed **LFUS 17685 387 to LFUS 17685 358** --- C Phase of terminal pole 17685 blew bad cable switched around isolated cable all cust back in tsmit29 | -90.0988 | 30.0187 | 70124 | A | Council District A | Joseph Giarrusso
1300916900 | NO | ORLEANS | COLD | 2018-12-11 23:28 | 2018-12-12 00:31 | 2018-12-12 02:03 | 912_2 | ENOI | TFUS | 1496143 | 3990847229 | DLIN | 1 | 2 | 0 | 0 | HUMAN FACTORS | HECD | Company - Distribution Line (Describe in remarks) | N | Changed **TFUS 1496143 28 to ERR 1496143 [count]** --- apt complex has meter pan marked wrong and the cut out disrupted the wrong cust. dsmit36 | -90.0732 | 29.9596 | 70112 | C | Council District C | Joseph Giarrusso
1302026355 | Yes | EAST ORLEANS | FAIR | 2019-01-04 10:26 | 2019-01-04 10:35 | 2019-01-04 11:10 | 2214 | ENOI | TFUS | 502667 | 43352505210 | DLIN | 6 | 3 | 132 | 44 | HUMAN FACTORS | HECD | Company - Distribution Line (Describe in remarks) | N | switching underground | -89.9632 | 30.049 | 70128 | E | Council District E | Kristin Palmer
1301736391 | Yes | ORLEANS | THDR | 2018-12-27 14:51 | 2018-12-27 16:35 | 2018-12-27 17:00 | 2021 | ENOI | TFUS | 1129306 | 3972646672 | DLIN | 1 | 7 | 903 | 129 | HUMAN FACTORS | HECD | Company - Distribution Line (Describe in remarks) | N | crew repaired jumper on disconnet switch had out for safety | -90.0791 | 29.9443 | 70113 | B | Council District B | Kristin Palmer
1302725175 | Yes | ORLEANS | FAIR | 2019-01-28 13:00 | 2019-01-28 13:34 | 2019-01-28 13:44 | 2013 | ENOI | DIS | 23148 | 3839846798 | DLIN | 1 | 188 | 8272 | 44 | HUMAN FACTORS | HECD | Company - Distribution Line (Describe in remarks) | N | Crew took outage to repair jumper on double circut feeder | -90.121 | 29.9481 | 70118 | A | Council District A | Kristin Palmer
1302632908 | Yes | ALGIERS | THDR | 2019-01-23 19:17 | 2019-01-23 19:17 | 2019-01-23 21:48 | W1726 | ENOI | TFUS | BY15557 | 4213446289 | DLIN | 81 | 2 | 300 | 150 | HUMAN FACTORS | HCDC | Contractor - Distribution Line (Describe in remarks) | N | Changed **TFUS BY15557 2 to TFUS BY15557 1** --- both 3 pot banks out bc crew wanted the customer s electrician to check rotation b4 energizing/ out from crew work earlier today nwashi1 | -90.0032 | 29.9331 | 70131 | C | Council District C | Jared Brossett
1301153950 | Yes | EAST ORLEANS | FAIR | 2018-12-17 08:52 | 2018-12-17 08:52 | 2018-12-17 11:40 | 2216 | ENOI | SERV | 1003372 | 42933502288 | DLIN | 6 | 1 | 168 | 168 | OTHER | CORR | Corrosion | N | hot leg broke in transformer vualt repaired leg and got great voltage dwillin | -89.9764 | 30.0411 | 70127 | E | Council District E | Jared Brossett
1302246618 | Yes | ORLEANS | FAIR | 2019-01-15 20:29 | 2019-01-15 21:38 | 2019-01-15 21:54 | 1926 | ENOI | DIS | 23936 | 3871346576 | DLIN | 1 | 2 | 170 | 85 | OTHER | EMER | Emergency Switching | N | b phase down in trees crew made repairs Fdr 2016 | -90.1111 | 29.9421 | 70115 | A | Council District A | Jared Brossett
1301772363 | Yes | ORLEANS | FAIR | 2018-12-28 04:24 | 2018-12-28 04:24 | 2018-12-28 04:51 | 407 | ENOI | TFUS | 1546406 | 38565483686 | DLIN | 1 | 11 | 297 | 27 | OTHER | EMER | Emergency Switching | N | Emergency Switching drop out due to tree burning | -90.1152 | 29.9913 | 70124 | A | Council District A | Jared Brossett
1302246529 | Yes | ORLEANS | FAIR | 2019-01-15 20:15 | 2019-01-15 21:32 | 2019-01-15 21:59 | 2016 | ENOI | DIS | 37171 | 3869446589 | DLIN | 1 | 35 | 3640 | 104 | OTHER | EMER | Emergency Switching | N | Wire down in trees this section isolated for saftey it is the bottom feeder | -90.1117 | 29.9424 | 70115 | A | Council District A | Cyndi Nguyen
1302247559 | Yes | ORLEANS | FAIR | 2019-01-15 20:29 | 2019-01-15 21:33 | 2019-01-15 22:24 | 1926 | ENOI | DIS | 27654 | 3872546552 | DLIN | 1 | 113 | 22995 | 115 | OTHER | EMER | Emergency Switching | N | bphase down in trees crew repaired Fdr 2016 | -90.1106 | 29.9413 | 70115 | A | Council District A | Joseph Giarrusso
1302008029 | Yes | ORLEANS | THDR | 2019-01-03 20:01 | 2019-01-03 20:38 | 2019-01-03 20:40 | 1926 | ENOI | DIS | 25096 | 3857046257 | DLIN | 1 | 144 | 6336 | 39 | OTHER | EMER | Emergency Switching | N | switching to isolate trouble | -90.1157 | 29.9332 | 70115 | A | Council District A | Jay Banks
1301506936 | Yes | ORLEANS | FAIR | 2018-12-24 21:56 | 2018-12-24 21:56 | 2018-12-24 22:14 | 406 | ENOI | DIS | 13919 | 3907049351 | DLIN | 1 | 331 | 21468 | 18 | OTHER | EMER | Emergency Switching | N | had to open disconect to isolate tp 17685 | -90.0988 | 30.0182 | 70124 | A | Council District A | Jared Brossett
1302247471 | Yes | ORLEANS | FAIR | 2019-01-15 20:29 | 2019-01-15 20:43 | 2019-01-15 21:28 | 1926 | ENOI | DIS | 24135 | 3888146476 | DLIN | 1 | 426 | 25134 | 59 | OTHER | EMER | Emergency Switching | N | b phase down in trees crew repaired Fdr 2016 | -90.1057 | 29.9392 | 70115 | B | Council District B | Jared Brossett
1301575210 | Yes | ORLEANS | THDR | 2018-12-26 22:43 | 2018-12-26 22:51 | 2018-12-26 22:51 | 401 | ENOI | SBKR | 401 | 3847049126 | DLIN | 1 | 562 | 4496 | 8 | OTHER | EMER | Emergency Switching | N | tree on line burning had to drop feeder due to burning | -90.1178 | 30.0182 | 70124 | A | Council District A | Jared Brossett
1301035624 | Yes | ALGIERS | COLD | 2018-12-15 02:44 | 2018-12-15 03:04 | 2018-12-15 03:00 | W1714 | ENOI | SBKR | W1714 | 4283945922 | DLIN | 81 | 1524 | 24384 | 16 | OTHER | EMER | Emergency Switching | N | Emergency Switching DUP TICKET#1301034838, 1301035168, 1301036330 (AKS) | -89.9811 | 29.9228 | 70131 | C | Council District C | Jared Brossett
1302293987 | Yes | ALGIERS | FAIR | 2019-01-18 07:05 | 2019-01-18 07:05 | 2019-01-18 08:07 | W0725 | ENOI | TFUS | 607363 | 4130046427 | DLIN | 81 | 1 | 62 | 62 | EQUIPMENT | EARR | Equipment - Arrestor | N | failed arrestor on transformer in rear/ cut clear/ refused ok nwashi1 | -90.0294 | 29.9371 | 70114 | C | Council District C | Jared Brossett
1301388110 | Yes | EAST ORLEANS | RAIN | 2018-12-20 01:03 | 2018-12-20 01:03 | 2018-12-20 05:08 | 616 | ENOI | TFUS | 1364627 | 41336486250 | DLIN | 6 | 1 | 245 | 245 | EQUIPMENT | EARR | Equipment - Arrestor | N | blown arrestor on transformer/cleared refused ok dfahr | -90.0275 | 29.9975 | 70126 | D | Council District D | Jared Brossett
1302187492 | Yes | ORLEANS | FAIR | 2019-01-12 14:56 | 2019-01-12 15:20 | 2019-01-12 16:00 | 2027 | ENOI | LFUS | 35103 | 3870647295 | DLIN | 1 | 12 | 768 | 64 | EQUIPMENT | EARR | Equipment - Arrestor | N | found arrestor tracking, removed from line and refused ok | -90.1112 | 29.9618 | 70125 | B | Council District B | Jared Brossett
1301598003 | Yes | ORLEANS | THDR | 2018-12-27 01:07 | 2018-12-27 01:19 | 2018-12-27 01:48 | 907 | ENOI | LFUS | 22006 | 3975047543 | DLIN | 1 | 23 | 943 | 41 | EQUIPMENT | EARR | Equipment - Arrestor | N | arrestor on high side one span from lfus blew was tracking cleared arrestor refused A phase tsmit29 | -90.0782 | 29.9683 | 70119 | D | Council District D | Jay Banks
1302170711 | Yes | ORLEANS | COLD | 2019-01-11 16:02 | 2019-01-11 16:53 | 2019-01-11 17:13 | 1704 | ENOI | LFUS | 21661 | 4026948923 | DLIN | 1 | 49 | 3479 | 71 | EQUIPMENT | EARR | Equipment - Arrestor | N | cleared blown arrestor and refused line dsmit36 | -90.0612 | 30.006 | 70122 | D | Council District D | Joseph Giarrusso
1301596716 | Yes | ORLEANS | THDR | 2018-12-27 01:04 | 2018-12-27 02:14 | 2018-12-27 02:24 | 907 | ENOI | LFUS | 38003 | 3986247643 | DLIN | 1 | 157 | 12560 | 80 | EQUIPMENT | EARR | Equipment - Arrestor | N | Changed **LFUS 38003 218 to LFUS 38003 154** --- cleared blown arrestor refused a phase tsmit29 | -90.0743 | 29.971 | 70116 | D | Council District D | Jared Brossett
1301094864 | Yes | ORLEANS | FAIR | 2018-12-16 15:09 | 2018-12-16 15:16 | 2018-12-16 15:17 | B0525 | ENOI | SBKR | B0525 | 3788147072 | DLIN | 1 | 211 | 1688 | 8 | EQUIPMENT | EARR | Equipment - Arrestor | N | CONTRACT CREW WORKING AT TRANSFORMER 569751 PUT ONLINE AND BLEW ARRESTOR TAKING OUT FEEDER | -90.1218 | 29.9465 | 70118 | A | Council District A | Joseph Giarrusso
1300931730 | NO | ORLEANS | COLD | 2018-12-12 09:51 | 2018-12-12 09:51 | 2018-12-12 17:30 | 2022 | ENOI | SECO | SECONDARY | 38422475038 | DLIN | 1 | 1 | 0 | 0 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 66756 10 to ERR 66756 1** --- repaired bad connection at pole dsmit36 | -90.12 | 29.9675 | 70118 | A | Council District A | Jared Brossett
1301821755 | NO | ORLEANS | FAIR | 2018-12-30 10:06 | 2018-12-30 10:06 | 2018-12-30 11:23 | 903 | ENOI | SECO | SECONDARY | 39074477190 | DLIN | 1 | 1 | 0 | 0 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 76403 * 6 to ERR 76403 * 6** --- repaired bad connection at pole. restored proper voltage dsmit36 | -90.0992 | 29.9734 | 70119 | A | Council District A | Joseph Giarrusso
1301757959 | Yes | EAST ORLEANS | FAIR | 2018-12-27 18:03 | 2018-12-27 18:03 | 2018-12-27 19:06 | 1608 | ENOI | TFUS | 1052363 | 4175348603 | DLIN | 6 | 1 | 63 | 63 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | replaced taop on terminal pole.. tbrock | -90.0144 | 29.9968 | 70126 | E | Council District E | Cyndi Nguyen
1300871956 | Yes | EAST ORLEANS | COLD | 2018-12-10 12:55 | 2018-12-10 13:03 | 2018-12-10 14:00 | 626 | ENOI | TFUS | 61784 | 41098482837 | DLIN | 6 | 1 | 65 | 65 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 61784 4 to SERV 61784 1** --- hot leg burned at pole-made repairs-cust back on-voltage ok-121/120/241 swalsh1 | -90.0353 | 29.9882 | 70126 | D | Council District D | Jay Banks
1301045416 | Yes | EAST ORLEANS | FAIR | 2018-12-15 15:35 | 2018-12-15 15:35 | 2018-12-15 16:40 | 625 | ENOI | SERV | 58586 | 40783487493 | DLIN | 6 | 1 | 65 | 65 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | changed out connections at weather head check voltgae ok 242 121-121 customer back on cschexn | -90.0449 | 30.0011 | 70126 | D | Council District D | Jared Brossett
1300602137 | Yes | EAST ORLEANS | FAIR | 2018-12-03 18:39 | 2018-12-03 18:39 | 2018-12-03 19:46 | 1710 | ENOI | TFUS | 65583 | 40440485348 | DLIN | 6 | 1 | 67 | 67 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 65583 7 to SERV 65583 1** --- hot leg connection heating up at weatherhead-changed all 3 connections-voltage ok-cust back on swalsh1 12-3-18 swalsh1 | -90.0558 | 29.9953 | 70122 | D | Council District D | #N/A
1300674924 | Yes | EAST ORLEANS | FAIR | 2018-12-06 17:07 | 2018-12-06 17:07 | 2018-12-06 18:20 | 1611 | ENOI | SERV | SERVICE | 43022493424 | DLIN | 6 | 1 | 73 | 73 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 63653 1 to SERV 63653 1** --- Replaced secondary connector at pole jvickna | -89.974 | 30.0168 | 70127 | E | Council District E | Cyndi Nguyen
1301043593 | Yes | EAST ORLEANS | FAIR | 2018-12-15 12:51 | 2018-12-15 12:51 | 2018-12-15 14:13 | 507 | ENOI | TFUS | 1529116 | 41314490240 | DLIN | 6 | 1 | 82 | 82 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | replaced connection at ct dropped out transfomer bank to make repairs repairs made re energized check voltage ok checked w dot bridge back in lights cschexn | -90.0282 | 30.0084 | 70126 | D | Council District D | Joseph Giarrusso
1302128521 | Yes | EAST ORLEANS | FAIR | 2019-01-09 16:08 | 2019-01-09 16:08 | 2019-01-09 17:39 | 613 | ENOI | SERV | SERVICE | 40588480120 | DLIN | 6 | 1 | 91 | 91 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | changed pole conects.. tbrock | -90.0514 | 29.981 | 70117 | D | Council District D | Joseph Giarrusso
1302150207 | Yes | ORLEANS | FAIR | 2019-01-10 13:44 | 2019-01-10 13:44 | 2019-01-10 15:17 | 1709 | ENOI | SERV | SERVICE | 39711481817 | DLIN | 1 | 1 | 93 | 93 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 28815 2 to SERV 28815 [count]** --- changed connection on pole advised jbologn | -90.079 | 29.9859 | 70119 | A | Council District A | Jay Banks
1302141182 | Yes | ORLEANS | FAIR | 2019-01-10 08:59 | 2019-01-10 08:59 | 2019-01-10 10:57 | 1704 | ENOI | SERV | SERVICE | 39541487343 | DLIN | 1 | 1 | 118 | 118 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 573311 * 32 to SERV 573311 * 1** --- repaired connection in manhole jbologn | -90.0842 | 30.0012 | 70122 | A | Council District A | Jay Banks
1301759426 | Yes | ALGIERS | WIND | 2018-12-27 18:32 | 2018-12-27 18:32 | 2018-12-27 20:37 | W1726 | ENOI | SERV | SERVICE | 4215645917 | DLIN | 81 | 1 | 125 | 125 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 1061765 16 to SERV 1061765 1** --- changed bad weatherhead connection mtaruc | -90.0026 | 29.9228 | 70131 | C | Council District C | Jared Brossett
1302692463 | Yes | ORLEANS | FAIR | 2019-01-26 12:20 | 2019-01-26 13:16 | 2019-01-26 14:40 | 2026 | ENOI | SERV | SERVICE | 38682476596 | DLIN | 1 | 1 | 140 | 140 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 68500 11 to SERV 68500 11** --- no lights out replaced connection at house tsmit29 | -90.1116 | 29.9718 | 70118 | A | Council District A | Jay Banks
1302244563 | Yes | EAST ORLEANS | FAIR | 2019-01-15 16:44 | 2019-01-15 17:55 | 2019-01-15 19:42 | 2212 | ENOI | SECO | SECONDARY | 41595498988 | DLIN | 6 | 1 | 178 | 178 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | secondary conect/ repaired.. tbrock | -90.0189 | 30.0326 | 70126 | E | Council District E | Joseph Giarrusso
1300900448 | Yes | EAST ORLEANS | FAIR | 2018-12-11 11:00 | 2018-12-11 11:00 | 2018-12-11 14:01 | 1009 | ENOI | SERV | SERVICE | 41494495505 | DLIN | 6 | 1 | 181 | 181 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | Changed **TFUS 27359 10 to SERV 27359 1** --- cust saw hot leg connection burning at pole feeding 6943 deanne-repaired hot leg-cust back on jvickna | -90.0223 | 30.0229 | 70126 | D | Council District D | Joseph Giarrusso
1302490722 | Yes | ORLEANS | WIND | 2019-01-19 23:43 | 2019-01-19 23:43 | 2019-01-20 00:34 | 1554 | ENOI | TFUS | 1093619 | 39316463794 | DLIN | 1 | 4 | 204 | 51 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | jumper came loose fixed and now everyone is back in lights jcox7 | -90.092 | 29.9364 | 70115 | B | Council District B | Cyndi Nguyen
1302482087 | Yes | ORLEANS | WIND | 2019-01-19 20:58 | 2019-01-19 20:58 | 2019-01-19 22:51 | B0525 | ENOI | TFUS | 3007168 | 38090469830 | DLIN | 1 | 9 | 1017 | 113 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | reconnected 1 hot leg jcox7 | -90.1307 | 29.9533 | 70118 | A | Council District A | Joseph Giarrusso
1300885742 | Yes | ORLEANS | COLD | 2018-12-10 23:24 | 2018-12-10 23:42 | 2018-12-11 00:10 | 613 | ENOI | TFUS | 56326 | 40047477797 | DLIN | 1 | 17 | 782 | 46 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | transformer lead burned itself in the clear. repaired and restored proper voltage dsmit36 | -90.0686 | 29.9746 | 70116 | D | Council District D | Jay Banks
1302485820 | Yes | ORLEANS | WIND | 2019-01-19 21:50 | 2019-01-19 22:38 | 2019-01-20 00:32 | 1554 | ENOI | TFUS | 61154 | 39323463699 | DLIN | 1 | 29 | 4698 | 162 | Summary Missing | ECON | Equipment - Connector / Sleeve | N | jumper came loose, fixed connection and everyone is back in lights jcox7 | -90.0918 | 29.9362 | 70115 | B | Council District B | Kristin Palmer
1302688671 | Yes | ORLEANS | FAIR | 2019-01-26 07:37 | 2019-01-26 07:37 | 2019-01-26 08:55 | 2016 | ENOI | SERV | SERVICE | 38410474207 | DLIN | 1 | 1 | 78 | 78 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | one leg open | -90.1204 | 29.9652 | 70118 | A | Council District A | Jay Banks
1302319523 | Yes | EAST ORLEANS | FAIR | 2019-01-18 17:37 | 2019-01-18 18:05 | 2019-01-18 19:00 | 613 | ENOI | SECO | SSERVICE | 4055548010 | DLIN | 6 | 1 | 747 | 83 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | Changed **LFUS 27803 82 to SECO 27803 82** --- repaired secondary conection.. tbrock | -90.0524 | 29.9809 | 70117 | D | Council District D | Joseph Giarrusso
1300703482 | Yes | EAST ORLEANS | FAIR | 2018-12-07 20:29 | 2018-12-07 20:29 | 2018-12-07 21:57 | 1710 | ENOI | SERV | SERVICE | 40516486405 | DLIN | 6 | 1 | 87 | 87 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | Changed **TFUS 57329 * 7 to SERV 57329 * 2** --- Replaced 2 hot leg and neutral connection at pole jvickna | -90.0534 | 29.9983 | 70122 | D | Council District D | Joseph Giarrusso
1300852122 | Yes | EAST ORLEANS | COLD | 2018-12-09 21:59 | 2018-12-09 21:59 | 2018-12-09 23:43 | 2213 | ENOI | SERV | 618882 | 44576508234 | DLIN | 6 | 1 | 104 | 104 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | Changed **TFUS 618882 5 to SERV 618882 5** --- Replaced hot leg connection in hand hole jvickna | -89.9243 | 30.057 | 70129 | E | Council District E | Kristin Palmer
1301352559 | Yes | EAST ORLEANS | FAIR | 2018-12-19 12:19 | 2018-12-19 12:19 | 2018-12-19 14:21 | 2215 | ENOI | SERV | 61816 | 42903506197 | DLIN | 6 | 1 | 122 | 122 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | Changed **TFUS 61816 9 to SERV 61816 9** --- Replaced hot leg connector and wire at pole jvickna | -89.9773 | 30.0519 | 70127 | E | Council District E | Jared Brossett
1301042085 | Yes | ORLEANS | COLD | 2018-12-15 11:34 | 2018-12-15 11:34 | 2018-12-15 13:57 | 2147 | ENOI | SERV | 1453098 | 39841459788 | DLIN | 1 | 1 | 142 | 142 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | Changed **TFUS 1453098 19 to SERV 1453098 19** --- loose connection at pole abengst | -90.0758 | 29.9253 | 70130 | B | Council District B | Jared Brossett
1302253893 | Yes | EAST ORLEANS | FAIR | 2019-01-16 09:44 | 2019-01-16 09:44 | 2019-01-16 14:57 | 623 | ENOI | SERV | SERVICE | 40438474026 | DLIN | 6 | 1 | 313 | 313 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | connection on wilson rack burned up canged oput connection and checked voltage got awesomne vooltage and spoke to csutomer dwillin | -90.0564 | 29.9642 | 70117 | C | Council District C | Jared Brossett
1301646867 | Yes | EAST ORLEANS | FAIR | 2018-12-27 07:21 | 2018-12-27 07:21 | 2018-12-27 13:12 | 1203 | ENOI | TFUS | 75786 | 44488493477 | DLIN | 6 | 1 | 351 | 351 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | fuse blew on b phase transformer switch and riser burned off the top of switch-dropped out other two switches and made repairs-refused bank ok-voltage ok-cust back on swalsh1 12-27-18 swalsh1 | -89.928 | 30.0164 | 70129 | E | Council District E | Jay Banks
1300641430 | Yes | ORLEANS | FAIR | 2018-12-05 10:32 | 2018-12-05 10:32 | 2018-12-05 16:46 | 1554 | ENOI | SERV | 79237 | 38870462985 | DLIN | 1 | 1 | 374 | 374 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | bad connector at pole | -90.1062 | 29.9343 | 70115 | B | Council District B | Jared Brossett
1302281525 | Yes | ORLEANS | RAIN | 2019-01-17 09:29 | 2019-01-17 09:31 | 2019-01-17 11:03 | 2021 | ENOI | TFUS | 62635 | 39299467093 | DLIN | 1 | 7 | 658 | 94 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | 1 span #2 cu. burnt down at sleeve repared advised jbologn | -90.0925 | 29.9454 | 70125 | B | Council District B | Kristin Palmer
1302194259 | Yes | EAST ORLEANS | FAIR | 2019-01-13 08:05 | 2019-01-13 08:14 | 2019-01-13 08:13 | 502 | ENOI | TFUS | 32702 | 40548491479 | DLIN | 6 | 9 | 72 | 8 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | looks like connection burnt secondary down | -90.0523 | 30.0122 | 70122 | D | Council District D | Joseph Giarrusso
1301633252 | Yes | ORLEANS | WIND | 2018-12-27 05:26 | 2018-12-27 07:52 | 2018-12-27 12:36 | 1916 | ENOI | TFUS | 64548 | 38687468303 | DLIN | 1 | 11 | 4730 | 430 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | trans. riser came out of trans refused ok jbologn | -90.1118 | 29.9491 | 70125 | A | Council District A | Joseph Giarrusso
1302603297 | Yes | EAST ORLEANS | FAIR | 2019-01-23 06:32 | 2019-01-23 08:04 | 2019-01-23 08:45 | 613 | ENOI | LFUS | 66342 | 4049947916 | DLIN | 6 | 81 | 10773 | 133 | EQUIPMENT | ECNS | Equipment - Connector Sleeve | N | repaired burned off jumper on bottom of 100amp cut out. dmorehe | -90.0541 | 29.9783 | 70117 | D | Council District D | Joseph Giarrusso
1302475302 | Yes | EAST ORLEANS | FAIR | 2019-01-19 19:21 | 2019-01-19 19:40 | 2019-01-20 01:15 | 1612 | ENOI | TFUS | 1571637 | 43078492189 | DLIN | 6 | 1 | 354 | 354 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -89.9729 | 30.0132 | 70127 | E | Council District E | Cyndi Nguyen
1301758893 | Yes | ORLEANS | THDR | 2018-12-27 18:20 | 2018-12-27 18:20 | 2018-12-27 19:15 | 1925 | ENOI | TFUS | 1102133 | 38997464057 | DLIN | 1 | 2 | 110 | 55 | EQUIPMENT | EARM | Equipment - Crossarm | N | CREW TO REPLACE ARM...complete | -90.1022 | 29.9372 | 70115 | B | Council District B | Joseph Giarrusso
1302490367 | Yes | EAST ORLEANS | FAIR | 2019-01-19 23:24 | 2019-01-19 23:56 | 2019-01-20 01:15 | 1612 | ENOI | LFUS | 93349 | 4310949215 | DLIN | 6 | 5 | 555 | 111 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -89.9714 | 30.0133 | 70127 | E | Council District E | Cyndi Nguyen
1301782495 | Yes | ORLEANS | THDR | 2018-12-28 10:34 | 2018-12-28 10:37 | 2018-12-28 13:35 | 1712 | ENOI | TFUS | 56219 | 39774477586 | DLIN | 1 | 8 | 1448 | 181 | EQUIPMENT | EARM | Equipment - Crossarm | N | replaced crossarm and got transformer back in | -90.0771 | 29.9743 | 70119 | D | Council District D | Jared Brossett
1302461163 | Yes | EAST ORLEANS | WIND | 2019-01-19 17:34 | 2019-01-19 18:17 | 2019-01-19 20:44 | 1708 | ENOI | TFUS | 67872 | 40397486146 | DLIN | 6 | 8 | 1520 | 190 | EQUIPMENT | EARM | Equipment - Crossarm | N | secondary down in alley, 2 TICKETS FOR SAME ISSUE, COMBING TIME | -90.0573 | 29.9976 | 70122 | D | Council District D | Joseph Giarrusso
1302502858 | Yes | EAST ORLEANS | FAIR | 2019-01-20 10:27 | 2019-01-20 10:27 | 2019-01-20 11:00 | 625 | ENOI | TFUS | 680284 | 40867487678 | DLIN | 6 | 9 | 297 | 33 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew changed out secondary arm, customers back on | -90.0423 | 30.0017 | 70126 | D | Council District D | Kristin Palmer
1302602671 | Yes | ORLEANS | FAIR | 2019-01-23 03:07 | 2019-01-23 07:57 | 2019-01-23 08:40 | 2016 | ENOI | TFUS | 65761 | 38308472895 | DLIN | 1 | 9 | 2997 | 333 | EQUIPMENT | EARM | Equipment - Crossarm | N | replaced arm and customers back on | -90.1237 | 29.9618 | 70118 | A | Council District A | Cyndi Nguyen
1300541341 | Yes | ORLEANS | FAIR | 2018-12-01 10:03 | 2018-12-01 11:37 | 2018-12-01 17:32 | 407 | ENOI | TFUS | 1546406 | 38565483686 | DLIN | 1 | 11 | 4939 | 449 | EQUIPMENT | EARM | Equipment - Crossarm | N | Broken Wilson rack, crew to replace | -90.1152 | 29.9913 | 70124 | A | Council District A | Cyndi Nguyen
1300843486 | Yes | EAST ORLEANS | FAIR | 2018-12-09 16:39 | 2018-12-09 16:39 | 2018-12-09 19:06 | 1710 | ENOI | TFUS | 1341479 | 40611487055 | DLIN | 6 | 15 | 2205 | 147 | EQUIPMENT | EARM | Equipment - Crossarm | N | Crew replaced crossarm | -90.0504 | 30 | 70122 | D | Council District D | Joseph Giarrusso
1302359400 | Yes | ORLEANS | THDR | 2019-01-19 05:53 | 2019-01-19 07:45 | 2019-01-19 11:09 | 1704 | ENOI | TFUS | 64964 | 39555486801 | DLIN | 1 | 15 | 4740 | 316 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to replace broken wilson rack | -90.0837 | 29.9995 | 70122 | D | Council District D | Cyndi Nguyen
1301717258 | Yes | ORLEANS | THDR | 2018-12-27 12:59 | 2018-12-27 13:19 | 2018-12-27 16:14 | 2022 | ENOI | TFUS | 66177 | 38305474688 | DLIN | 1 | 16 | 3120 | 195 | EQUIPMENT | EARM | Equipment - Crossarm | N | wilson rack fell got together tokk out xfmr. repaired wilson rack refused xfmr tsmit29 | -90.1237 | 29.9666 | 70118 | A | Council District A | Joseph Giarrusso
1301361653 | Yes | ORLEANS | FAIR | 2018-12-19 13:22 | 2018-12-19 13:22 | 2018-12-19 13:41 | 1922 | ENOI | TFUS | 63542 | 39373457410 | DLIN | 1 | 18 | 342 | 19 | EQUIPMENT | EARM | Equipment - Crossarm | N |  | -90.0905 | 29.9189 | 70115 | B | Council District B | Joseph Giarrusso
1301617138 | Yes | ORLEANS | THDR | 2018-12-27 03:10 | 2018-12-27 03:34 | 2018-12-27 05:13 | B0527 | ENOI | LFUS | 21185 | 3807446657 | DLIN | 1 | 35 | 4305 | 123 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to change crossarm | -90.1311 | 29.9444 | 70118 | A | Council District A | Cyndi Nguyen
1302618841 | Yes | ORLEANS | THDR | 2019-01-23 11:02 | 2019-01-23 12:35 | 2019-01-23 14:10 | 2013 | ENOI | LFUS | 38501 | 3830146744 | DLIN | 1 | 44 | 8272 | 188 | EQUIPMENT | EARM | Equipment - Crossarm | N | replaced broke double dead end arms, customers back in | -90.1242 | 29.9467 | 70118 | A | Council District A | Cyndi Nguyen
1301772717 | Yes | ORLEANS | THDR | 2018-12-28 03:26 | 2018-12-28 07:51 | 2018-12-28 08:01 | 1924 | ENOI | LFUS | 27637 | 3917746081 | DLIN | 1 | 52 | 14300 | 275 | EQUIPMENT | EARM | Equipment - Crossarm | N | Equipment - Crossarm CREW TO REPLACE CROSSARM | -90.0967 | 29.9283 | 70115 | B | Council District B | Jay Banks
1301575639 | Yes | ORLEANS | THDR | 2018-12-26 22:54 | 2018-12-26 23:04 | 2018-12-27 03:02 | 1916 | ENOI | LFUS | 277702 | 3876246570 | DLIN | 1 | 66 | 16368 | 248 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to replace | -90.1094 | 29.9417 | 70125 | B | Council District B | Kristin Palmer
1301607083 | Yes | EAST ORLEANS | WIND | 2018-12-27 02:08 | 2018-12-27 07:43 | 2018-12-27 07:46 | 622 | ENOI | LFUS | 27886 | 4087447744 | DLIN | 6 | 237 | 80106 | 338 | EQUIPMENT | EARM | Equipment - Crossarm | N | crew to change cross arm at location...complete | -90.0425 | 29.9735 | 70117 | D | Council District D | Joseph Giarrusso
1301774569 | NO | ORLEANS | RAIN | 2018-12-28 07:19 | 2018-12-28 07:44 | 2018-12-28 07:20 | 1712 | ENOI | SBKR | 1712 | 4023848726 | DLIN | 1 | 3153 | 3153 | 1 | EQUIPMENT | EARM | Equipment - Crossarm | N | Barracks St. & N. Dorgenois St, X-arm braces broke BREAKER OPERATED ONE TIME AND CLOSED @ 0719 | -90.0622 | 30.0007 | 70122 | D | Council District D | Joseph Giarrusso
1302016853 | Yes | EAST ORLEANS | FAIR | 2019-01-04 01:52 | 2019-01-04 04:09 | 2019-01-04 05:26 | 2214 | ENOI | LFUS | 25651 | 4338850670 | DLIN | 6 | 19 | 4047 | 213 | EQUIPMENT | EELB | Equipment - Elbow | N | Crews replaced 2 failed cable cure elbows & failed transformer | -97.0758 | 27.9066 | 70128 | E | Council District E | Joseph Giarrusso
1301866678 | Yes | EAST ORLEANS | THDR | 2018-12-31 09:32 | 2018-12-31 11:21 | 2018-12-31 11:45 | 2214 | ENOI | LFUS | 25878 | 4309450396 | DLIN | 6 | 54 | 7182 | 133 | EQUIPMENT | EELB | Equipment - Elbow | N | bad elbow in pad | -97.0758 | 27.9066 | 70128 | E | Council District E | Joseph Giarrusso
1302474902 | Yes | ORLEANS | WIND | 2019-01-19 19:14 | 2019-01-19 19:14 | 2019-01-19 20:35 | 2012 | ENOI | TFUS | 1456562 | 38907480783 | DLIN | 1 | 1 | 81 | 81 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused a phase and took slack out of sheild jcox7 | -90.1045 | 29.9832 | 70119 | A | Council District A | Jay Banks
1300866982 | Yes | ORLEANS | COLD | 2018-12-10 10:32 | 2018-12-10 10:32 | 2018-12-10 13:51 | 509 | ENOI | TFUS | 17529 | 39577492792 | DLIN | 1 | 7 | 1393 | 199 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | weak fuse link refused ok advised jbologn | -90.0829 | 30.0161 | 70122 | D | Council District D | Jay Banks
1301001868 | Yes | ORLEANS | FAIR | 2018-12-14 12:45 | 2018-12-14 16:25 | 2018-12-14 17:10 | 1917 | ENOI | TFUS | 77669 | 38571461101 | DLIN | 1 | 7 | 1855 | 265 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused ok. was fused with 10qr in 100. dsmit36 | -90.1158 | 29.9293 | 70115 | A | Council District A | Jay Banks
1301069783 | Yes | EAST ORLEANS | FAIR | 2018-12-16 08:22 | 2018-12-16 08:33 | 2018-12-16 09:31 | 502 | ENOI | TFUS | 50970 | 40624490794 | DLIN | 6 | 8 | 552 | 69 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refuse transformer ok customer back in lights cschexn | -90.0498 | 30.0103 | 70122 | D | Council District D | Jared Brossett
1302484239 | Yes | EAST ORLEANS | RAIN | 2019-01-19 21:21 | 2019-01-19 23:54 | 2019-01-20 00:13 | 2325 | ENOI | LFUS | 62254 | 4189647510 | DLIN | 6 | 17 | 2924 | 172 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused lattral fuse cbowden | -90.0103 | 29.9668 | 70117 | E | Council District E | Jared Brossett
1301512236 | Yes | ALGIERS | FAIR | 2018-12-25 08:50 | 2018-12-25 10:08 | 2018-12-25 11:06 | W1714 | ENOI | LFUS | 5591 | 4280645718 | DLIN | 81 | 32 | 4352 | 136 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Fuse link melted. Replaced fuse | -89.9822 | 29.9171 | 70131 | C | Council District C | Jared Brossett
1300815585 | Yes | EAST ORLEANS | COLD | 2018-12-09 08:25 | 2018-12-09 08:51 | 2018-12-09 09:31 | 1205 | ENOI | LFUS | 25848 | 4438450346 | DLIN | 6 | 39 | 2574 | 66 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused lateral 25848 in cub 300. chkd all transformers on loop B ph. looked in cub 305 as well. didnt see anything to take it out. refused ok atampl1 | -97.0758 | 27.9066 | 70129 | E | Council District E | Joseph Giarrusso
1301603814 | Yes | EAST ORLEANS | WIND | 2018-12-27 01:53 | 2018-12-27 02:18 | 2018-12-27 04:48 | 1702 | ENOI | LFUS | 21619 | 4071349042 | DLIN | 6 | 42 | 7350 | 175 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Lateral had no obvious damage, refused and held.. Lateral also runs in between feeder and high wind may have caused phases to touch. Locking feeder 513 out Refused back in lights mjack11 | -90.047 | 30.0092 | 70122 | D | Council District D | Joseph Giarrusso
1302713158 | Yes | EAST ORLEANS | FAIR | 2019-01-27 23:04 | 2019-01-28 00:52 | 2019-01-28 00:59 | 2223 | ENOI | LFUS | 27108 | 4397251427 | DLIN | 6 | 48 | 5520 | 115 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | patroled lateral refused ok everyboby back on cschexn | -89.9432 | 30.0738 | 70128 | E | Council District E | Jay Banks
1302480579 | Yes | EAST ORLEANS | RAIN | 2019-01-19 20:39 | 2019-01-19 21:47 | 2019-01-19 22:21 | 1611 | ENOI | LFUS | 21769 | 4296949346 | DLIN | 6 | 52 | 5304 | 102 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused latral customer back on cbowden | -89.9756 | 30.0168 | 70127 | E | Council District E | Cyndi Nguyen
1302490413 | Yes | EAST ORLEANS | RAIN | 2019-01-19 23:23 | 2019-01-20 03:41 | 2019-01-20 03:50 | 1611 | ENOI | LFUS | 21769 | 4296949346 | DLIN | 6 | 52 | 13884 | 267 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused lattral cbowden | -89.9756 | 30.0168 | 70127 | E | Council District E | Joseph Giarrusso
1300573530 | Yes | EAST ORLEANS | FAIR | 2018-12-02 09:09 | 2018-12-02 10:15 | 2018-12-02 10:31 | 1612 | ENOI | LFUS | 27885 | 4349649589 | DLIN | 6 | 63 | 5166 | 82 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refuse latteral no. 27885 cscale1 | -89.959 | 30.0234 | 70127 | E | Council District E | Cyndi Nguyen
1302488397 | Yes | ORLEANS | WIND | 2019-01-19 22:55 | 2019-01-19 23:40 | 2019-01-19 23:21 | 911 | ENOI | LFUS | 21551 | 3912247801 | DLIN | 1 | 80 | 2080 | 26 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused (A) phase jcox7 | -90.0979 | 29.9756 | 70119 | A | Council District A | Cyndi Nguyen
1302482384 | Yes | ORLEANS | WIND | 2019-01-19 21:01 | 2019-01-19 21:12 | 2019-01-19 21:57 | 911 | ENOI | LFUS | 21551 | 3912247801 | DLIN | 1 | 80 | 4480 | 56 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused (a) phase jcox7 | -90.0979 | 29.9756 | 70119 | A | Council District A | Kristin Palmer
1301431818 | Yes | ORLEANS | THDR | 2018-12-21 00:51 | 2018-12-21 01:19 | 2018-12-21 02:31 | 1513 | ENOI | LFUS | 21551 | 3912247801 | DLIN | 1 | 80 | 8000 | 100 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | REFUSE | -90.0979 | 29.9756 | 70119 | A | Council District A | Kristin Palmer
1302713167 | Yes | EAST ORLEANS | FAIR | 2019-01-27 23:07 | 2019-01-27 23:07 | 2019-01-28 01:03 | 2223 | ENOI | LFUS | 27108 | 43941513259 | DLIN | 6 | 103 | 11948 | 116 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | refused lateral 27108 cschexn | -89.9443 | 30.0709 | 70128 | E | Council District E | Cyndi Nguyen
1300660146 | Yes | EAST ORLEANS | COLD | 2018-12-06 08:58 | 2018-12-06 12:09 | 2018-12-06 13:21 | 1205 | ENOI | TFUS | 32814 | 44959501841 | DLIN | 6 | 159 | 41817 | 263 | EQUIPMENT | EFLK | Equipment - Fuse Link | N | Changed **TFUS 32814 161 to TFUS 32814 8** --- found transformer out at location feeding building 10. turned off disconnect switch and refused padmount. checked voltage 123/123/247. turned disconnect switch back on. all cust in build | -89.9125 | 30.0392 | 70129 | E | Council District E | Jay Banks
1302511029 | Yes | EAST ORLEANS | FAIR | 2019-01-20 16:52 | 2019-01-20 16:52 | 2019-01-20 19:20 | 625 | ENOI | TFUS | 1365739 | 41008488173 | DLIN | 6 | 2 | 296 | 148 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | switch riser | -90.0379 | 30.003 | 70126 | D | Council District D | Jay Banks
1301629732 | Yes | ORLEANS | THDR | 2018-12-27 04:25 | 2018-12-27 04:39 | 2018-12-27 05:31 | 1914 | ENOI | TFUS | 549774 | 38532459320 | DLIN | 1 | 12 | 792 | 66 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | riser burnt off top side of switch replaced riser cosed xfmr tsmit29 | -90.1171 | 29.9244 | 70115 | A | Council District A | Joseph Giarrusso
1301491753 | Yes | ALGIERS | FAIR | 2018-12-24 07:04 | 2018-12-24 07:04 | 2018-12-24 08:36 | W1726 | ENOI | LFUS | 33797 | 4270045926 | DLIN | 81 | 27 | 2484 | 92 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | changed out fuse switch at lat zwashin | -89.9854 | 29.9228 | 70131 | C | Council District C | Joseph Giarrusso
1302464725 | Yes | ALGIERS | WIND | 2019-01-19 18:00 | 2019-01-19 18:25 | 2019-01-19 18:41 | W0118 | ENOI | LFUS | 10182 | 4058446596 | DLIN | 81 | 35 | 1845 | 41 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | on site repairing switch | -90.052 | 29.942 | 70114 | C | Council District C | Joseph Giarrusso
1301814887 | Yes | EAST ORLEANS | FAIR | 2018-12-29 18:50 | 2018-12-29 20:54 | 2018-12-29 23:10 | 2214 | ENOI | LFUS | 25878 | 4309450396 | DLIN | 6 | 54 | 14040 | 260 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | Equipment - Fuse Switch | -97.0758 | 27.9066 | 70128 | E | Council District E | Kristin Palmer
1301861501 | Yes | EAST ORLEANS | RAIN | 2018-12-31 09:00 | 2018-12-31 09:24 | 2018-12-31 09:45 | 1604 | ENOI | LFUS | 27746 | 4273849388 | DLIN | 6 | 56 | 2520 | 45 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | made repairs | -89.9829 | 30.0181 | 70127 | E | Council District E | Jay Banks
1301608977 | Yes | EAST ORLEANS | THDR | 2018-12-27 02:27 | 2018-12-27 04:08 | 2018-12-27 04:32 | 513 | ENOI | SBKR | 513 | 4074749223 | DLIN | 6 | 99 | 12375 | 125 | EQUIPMENT | EFSW | Equipment - Fuse Switch | N | fuse switch 21619 failed and locked feeder out | -90.046 | 30.0142 | 70126 | D | Council District D | Jared Brossett
1301678625 | Yes | ORLEANS | WIND | 2018-12-27 05:24 | 2018-12-27 10:18 | 2018-12-27 12:15 | 907 | ENOI | LFUS | 27868 | 3966847557 | DLIN | 1 | 13 | 5343 | 411 | EQUIPMENT | EINS | Equipment - Insulator | N | failed insulator removed insulator turned in ticket to get corner structure repaired B phase insulator jdomang | -90.0806 | 29.9686 | 70119 | D | Council District D | Cyndi Nguyen
1301743873 | Yes | ORLEANS | THDR | 2018-12-27 15:36 | 2018-12-27 15:44 | 2018-12-27 16:00 | 1925 | ENOI | LFUS | 21515 | 3900646470 | DLIN | 1 | 110 | 2640 | 24 | EQUIPMENT | EINS | Equipment - Insulator | N | crew cleared insulator | -90.102 | 29.939 | 70115 | B | Council District B | Jay Banks
1301559694 | Yes | EAST ORLEANS | THDR | 2018-12-26 19:10 | 2018-12-26 20:42 | 2018-12-26 20:54 | 506 | ENOI | RCLR | 13917 | 4069649353 | DLIN | 6 | 280 | 29120 | 104 | EQUIPMENT | EINS | Equipment - Insulator | N | A phase fault insulator broke at location | -90.0527 | 30.0215 | 70122 | D | Council District D | Jared Brossett
1301566115 | Yes | EAST ORLEANS | FAIR | 2018-12-26 19:10 | 2018-12-26 21:20 | 2018-12-26 21:22 | 506 | ENOI | DIS | D01595 | 4068049496 | DLIN | 6 | 524 | 69168 | 132 | EQUIPMENT | EINS | Equipment - Insulator | N | A phase fault on insulator at Arts and Madrid causing outage on feeder | -90.0527 | 30.0215 | 70122 | D | Council District D | Cyndi Nguyen
1301561320 | Yes | EAST ORLEANS | THDR | 2018-12-26 19:58 | 2018-12-26 20:42 | 2018-12-26 20:56 | 506 | ENOI | SBKR | 506 | 4074749220 | DLIN | 6 | 621 | 36018 | 58 | EQUIPMENT | EINS | Equipment - Insulator | N | A phase fault at location Insulator failed | -90.0527 | 30.0215 | 70122 | D | Council District D | Cyndi Nguyen
1301850484 | Yes | EAST ORLEANS | RAIN | 2018-12-31 06:46 | 2018-12-31 08:24 | 2018-12-31 08:11 | 1604 | ENOI | RCLR | 24864 | 4288049405 | DLIN | 6 | 726 | 61710 | 85 | EQUIPMENT | EINS | Equipment - Insulator | N | c phase insulator for jumper at the corner of grant and gabriel failed feeding 2 phase lateral sw-27966--also one span down a squirrelcalled crew for repairs and energized recloser-24864-cust back on swalsh1 12/31/18 | -89.9785 | 30.0186 | 70127 | E | Council District E | Jared Brossett
1302765895 | Yes | ORLEANS | COLD | 2019-01-29 06:57 | 2019-01-29 15:44 | 2019-01-29 16:06 | 412 | ENOI | TFUS | 14632 | 38418482358 | DLIN | 1 | 4 | 2196 | 549 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | line side jummper burnt loose from switch reconnected jummper to switch apalomb | -90.1199 | 29.989 | 70124 | A | Council District A | Jared Brossett
1302556166 | Yes | ORLEANS | FAIR | 2019-01-22 13:35 | 2019-01-22 13:55 | 2019-01-22 15:04 | 1709 | ENOI | LFUS | 37636 | 3975948181 | DLIN | 1 | 66 | 5874 | 89 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | riser burnt off C phase lat. switch repaired advised jbologn | -90.0765 | 29.9858 | 70119 | A | Council District A | Kristin Palmer
1301573360 | Yes | EAST ORLEANS | FAIR | 2018-12-26 22:25 | 2018-12-26 23:14 | 2018-12-26 23:28 | 1607 | ENOI | LFUS | 21750 | 4237949491 | DLIN | 6 | 73 | 4599 | 63 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | pole grd hit phase/ refused.. tbrock | -89.9943 | 30.0209 | 70126 | E | Council District E | Kristin Palmer
1302480173 | Yes | EAST ORLEANS | WIND | 2019-01-19 20:21 | 2019-01-19 22:49 | 2019-01-19 23:04 | 1202 | ENOI | RCLR | 27973 | 4555150350 | DLIN | 6 | 75 | 12225 | 163 | EQUIPMENT | EOTH | Equipment - Other (Describe in Remarks Field) | N | shield wire down | -89.8938 | 30.0437 | 70129 | E | Council District E | Jared Brossett
1302603731 | Yes | ALGIERS | THDR | 2019-01-22 22:32 | 2019-01-23 07:51 | 2019-01-23 16:54 | W1726 | ENOI | OPEN | 4215146282 | 4215146282 | DLIN | 81 | 10 | 11020 | 1102 | EQUIPMENT | EPOL | Equipment - Pole | N | crew to replace pole | -90.0027 | 29.9329 | 70131 | C | Council District C | Joseph Giarrusso
1301439875 | Yes | EAST ORLEANS | FAIR | 2018-12-21 09:57 | 2018-12-21 10:08 | 2018-12-21 11:40 | 501 | ENOI | LFUS | 17804 | 4087549079 | DLIN | 6 | 14 | 1442 | 103 | EQUIPMENT | EPOL | Equipment - Pole | N | CRW ON SITE REPLACING POLE | -90.042 | 30.0102 | 70126 | D | Council District D | Cyndi Nguyen
1301715511 | Yes | EAST ORLEANS | THDR | 2018-12-27 12:54 | 2018-12-27 12:54 | 2018-12-27 16:01 | 2346 | ENOI | LFUS | 38435 | 4188147026 | DLIN | 6 | 16 | 2976 | 186 | EQUIPMENT | EPOL | Equipment - Pole | N | crew replaced broken pole | -90.0109 | 29.9534 | 70117 | E | Council District E | Joseph Giarrusso
1301863848 | Yes | ORLEANS | RAIN | 2018-12-31 08:41 | 2018-12-31 09:49 | 2018-12-31 11:10 | 400 | ENOI | DIS | 14785 | 3841449085 | DLIN | 1 | 29 | 4321 | 149 | EQUIPMENT | EPOL | Equipment - Pole | N | crew replaced broken pole at switch # 39481 on 32nd St. near Bellaire Dr. | -90.1197 | 30.0112 | 70124 | A | Council District A | Jared Brossett
1300562392 | Yes | ORLEANS | FAIR | 2018-12-01 10:03 | 2018-12-01 21:15 | 2018-12-01 21:11 | 407 | ENOI | LFUS | 17719 | 3856848407 | DLIN | 1 | 30 | 20010 | 667 | EQUIPMENT | EPOL | Equipment - Pole | N | crew changing out pole found bad while changing Wilson Rack | -90.1152 | 29.9923 | 70124 | A | Council District A | Jared Brossett
1302134872 | Yes | ORLEANS | FAIR | 2019-01-09 20:21 | 2019-01-09 23:17 | 2019-01-10 00:21 | 1712 | ENOI | LFUS | 57979 | 3980847827 | DLIN | 1 | 34 | 8160 | 240 | EQUIPMENT | EPOL | Equipment - Pole | N | top of pole caught fire crew to repair...crew got lateral back in but still working on two transformers..made serperate outages for those | -90.0761 | 29.976 | 70119 | D | Council District D | Jared Brossett
1302570245 | Yes | ALGIERS | FAIR | 2019-01-22 22:32 | 2019-01-23 06:32 | 2019-01-23 06:43 | W1726 | ENOI | LFUS | 33334 | 4215946276 | DLIN | 81 | 75 | 36750 | 490 | EQUIPMENT | EPOL | Equipment - Pole | N | crew to replace pole | -90.0024 | 29.9328 | 70131 | C | Council District C | Joseph Giarrusso
1302568398 | Yes | ALGIERS | FAIR | 2019-01-22 20:02 | 2019-01-22 23:25 | 2019-01-22 23:27 | W1713 | ENOI | DIS | 5142 | 4253745798 | DLIN | 81 | 108 | 22140 | 205 | EQUIPMENT | EPOL | Equipment - Pole | N |  | -89.9906 | 29.9195 | 70131 | C | Council District C | Joseph Giarrusso
1300594726 | Yes | ORLEANS | FAIR | 2018-12-03 12:58 | 2018-12-03 15:27 | 2018-12-03 14:15 | 2016 | ENOI | LFUS | 27919 | 3843846812 | DLIN | 1 | 160 | 12320 | 77 | EQUIPMENT | EPOL | Equipment - Pole | N | Crew isolated broken poles on Cohn, Audubon St. to Audubon Blvd.: Repairs made & remaining load restored at 8:pm | -90.1201 | 29.9487 | 70118 | A | Council District A | Jay Banks
1301859008 | Yes | ORLEANS | THDR | 2018-12-31 08:41 | 2018-12-31 09:03 | 2018-12-31 09:22 | 400 | ENOI | SBKR | 400 | 3847049127 | DLIN | 1 | 280 | 11480 | 41 | EQUIPMENT | EPOL | Equipment - Pole | N | replaced pole at 32 and bellaire | -90.1179 | 30.0122 | 70124 | A | Council District A | Jared Brossett
1301928198 | Yes | ALGIERS | FOGG | 2018-12-31 17:58 | 2018-12-31 21:11 | 2018-12-31 21:18 | W1714 | ENOI | RCLR | 1111 | 4223545490 | DLIN | 81 | 697 | 139400 | 200 | EQUIPMENT | EPOL | Equipment - Pole | N | back n brizzut | -90.0002 | 29.911 | 70131 | C | Council District C | Jared Brossett
1302034361 | Yes | EAST ORLEANS | FAIR | 2019-01-04 15:55 | 2019-01-04 15:55 | 2019-01-04 16:52 | 1608 | ENOI | TFUS | 1052363 | 4175348603 | DLIN | 6 | 1 | 57 | 57 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | switch riser broke offf/ repaired.. tbrock | -90.0144 | 29.9968 | 70126 | E | Council District E | Jared Brossett
1302829660 | Yes | EAST ORLEANS | FAIR | 2019-01-30 20:13 | 2019-01-30 20:13 | 2019-01-31 00:03 | 1001 | ENOI | SERV | SERVICE | 41735493289 | DLIN | 6 | 1 | 230 | 230 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | changed service.. tbrock | -90.0147 | 30.0168 | 70126 | D | Council District D | Kristin Palmer
1301037148 | Yes | EAST ORLEANS | FAIR | 2018-12-15 05:17 | 2018-12-15 05:17 | 2018-12-15 07:37 | 1204 | ENOI | TFUS | 1269557 | 50073540415 | DLIN | 6 | 2 | 280 | 140 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | hot line clamp came off of stirrup made repairs with hot stick refused ok customer back in lights cschexn | -89.7491 | 30.1434 | 70129 | E | Council District E | Joseph Giarrusso
1301811117 | Yes | ORLEANS | FAIR | 2018-12-29 13:20 | 2018-12-29 19:45 | 2018-12-29 22:11 | 407 | ENOI | LFUS | 38372 | 3864948304 | DLIN | 1 | 2 | 1062 | 531 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | bad cable, crew will repair | -90.1126 | 29.9896 | 70124 | A | Council District A | Joseph Giarrusso
1302552514 | Yes | ORLEANS | FAIR | 2019-01-22 11:31 | 2019-01-22 11:31 | 2019-01-22 14:55 | 2027 | ENOI | TFUS | 65578 | 38817472077 | DLIN | 1 | 4 | 816 | 204 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | 29 OTHER/MISCELLANEOUS SEND TO BUCKET...BOTH DOUBLES NO POWER COMING IN...APPEARS FUSE BLOWN djohn26 | -90.1075 | 29.9593 | 70125 | B | Council District B | Cyndi Nguyen
1302262002 | Yes | EAST ORLEANS | FAIR | 2019-01-16 13:20 | 2019-01-16 13:20 | 2019-01-16 16:55 | 2211 | ENOI | TFUS | 1541062 | 42160499295 | DLIN | 6 | 4 | 860 | 215 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | crew repaired burned up primary UG | -90.0011 | 30.0331 | 70126 | E | Council District E | Cyndi Nguyen
1301774195 | Yes | ALGIERS | FAIR | 2018-12-28 07:08 | 2018-12-28 08:33 | 2018-12-28 08:27 | W1725 | ENOI | LFUS | 33571 | 4257246092 | DLIN | 81 | 5 | 395 | 79 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | bottom side of cut out burned off, made repairs all back in | -89.9895 | 29.9274 | 70131 | C | Council District C | Cyndi Nguyen
1300895618 | Yes | EAST ORLEANS | FAIR | 2018-12-11 09:33 | 2018-12-11 09:33 | 2018-12-11 11:53 | 1204 | ENOI | DIS | 24216 | 4892351980 | DLIN | 6 | 5 | 700 | 140 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | wire down | -89.7865 | 30.0873 | 70129 | E | Council District E | Cyndi Nguyen
1302177215 | Yes | ORLEANS | FAIR | 2019-01-11 21:24 | 2019-01-11 21:24 | 2019-01-12 01:11 | 1705 | ENOI | XFMR | 68300 | 39691476583 | DLIN | 1 | 18 | 4086 | 227 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  |  |  | 70119 | D | Council District D | Kristin Palmer
1301950095 | Yes | ORLEANS | FAIR | 2019-01-01 11:58 | 2019-01-01 13:06 | 2019-01-01 16:18 | 1924 | ENOI | LFUS | 27827 | 3901046066 | DLIN | 1 | 24 | 6240 | 260 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Crew on the way to pick up down primary | -90.102 | 29.9279 | 70115 | B | Council District B | Cyndi Nguyen
1302246103 | Yes | ORLEANS | FAIR | 2019-01-15 19:00 | 2019-01-15 20:29 | 2019-01-15 20:30 | 1926 | ENOI | LFUS | 28112 | 3869346261 | DLIN | 1 | 36 | 3240 | 90 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | wire down, crew on site | -90.1117 | 29.9334 | 70115 | B | Council District B | Jared Brossett
1301432810 | Yes | ORLEANS | FAIR | 2018-12-21 01:35 | 2018-12-21 04:46 | 2018-12-21 05:59 | 510 | ENOI | LFUS | 17554 | 3995149310 | DLIN | 1 | 52 | 13728 | 264 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | WIRE DOWN | -90.0711 | 30.0168 | 70122 | D | Council District D | Jay Banks
1301813218 | Yes | ORLEANS | FAIR | 2018-12-29 16:28 | 2018-12-29 16:39 | 2018-12-29 16:46 | 407 | ENOI | LFUS | 21906 | 3864748399 | DLIN | 1 | 70 | 1260 | 18 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | went out when refuse underground section | -90.1125 | 29.9922 | 70124 | A | Council District A | Joseph Giarrusso
1301809981 | Yes | ORLEANS | FAIR | 2018-12-29 13:23 | 2018-12-29 14:36 | 2018-12-29 15:00 | 407 | ENOI | LFUS | 21906 | 3864748399 | DLIN | 1 | 70 | 6790 | 97 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | bad cable in underground section, isolated and overhead back on | -90.1125 | 29.9922 | 70124 | A | Council District A | Jay Banks
1302492666 | Yes | ALGIERS | COLD | 2019-01-20 01:34 | 2019-01-20 02:07 | 2019-01-20 03:22 | W0723 | ENOI | LFUS | 11508 | 4172346033 | DLIN | 81 | 92 | 9936 | 108 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | back n now brizzut | -90.0164 | 29.9262 | 70114 | C | Council District C | Joseph Giarrusso
1301938976 | Yes | ORLEANS | FAIR | 2019-01-01 08:08 | 2019-01-01 14:03 | 2019-01-01 13:16 | 1917 | ENOI | LFUS | 21084 | 3850746102 | DLIN | 1 | 93 | 28644 | 308 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Crew on the way to pick up down primary | -90.1178 | 29.929 | 70115 | A | Council District A | Joseph Giarrusso
1300890884 | Yes | EAST ORLEANS | FAIR | 2018-12-11 03:22 | 2018-12-11 09:49 | 2018-12-11 11:53 | 1204 | ENOI | OPEN | 4905452086 | 4905452086 | DLIN | 6 | 111 | 56721 | 511 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N |  | -89.7823 | 30.0901 | 70129 | E | Council District E | Jared Brossett
1301435747 | Yes | EAST ORLEANS | COLD | 2018-12-21 06:25 | 2018-12-21 06:25 | 2018-12-21 08:26 | 1010 | ENOI | LFUS | 37100 | 41458499139 | DLIN | 6 | 153 | 18513 | 121 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | Lateral out due to underground going out--Lateral 37100 back in jvickna | -90.0232 | 30.033 | 70126 | E | Council District E | Kristin Palmer
1301736030 | Yes | ORLEANS | WIND | 2018-12-27 14:27 | 2018-12-27 16:19 | 2018-12-27 16:55 | 2021 | ENOI | DIS | 23719 | 3951746704 | DLIN | 1 | 158 | 23384 | 148 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | jumper on b phase burned up here opened switch and repaired | -90.0856 | 29.9452 | 70113 | B | Council District B | Cyndi Nguyen
1301728715 | NO | ORLEANS | WIND | 2018-12-27 14:14 | 2018-12-27 14:16 | 2018-12-27 14:17 | 2021 | ENOI | SBKR | 2021 | 3847347396 | DLIN | 1 | 1172 | 3516 | 3 | CONDUCTOR | EPRI | Equipment - Primary Conductor | N | jumper failed at switch 23719...repairs made | -90.1184 | 29.9646 | 70118 | A | Council District A | Kristin Palmer
1302072714 | Yes | ORLEANS | FAIR | 2019-01-07 16:36 | 2019-01-07 16:36 | 2019-01-07 21:00 | 2017 | ENOI | XFMR | 74906 | 38877473101 | DLIN | 1 | 1 | 264 | 264 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.1057 | 29.9622 | 70125 | B | Council District B | Jay Banks
1300645035 | Yes | EAST ORLEANS | FAIR | 2018-12-05 13:25 | 2018-12-05 13:25 | 2018-12-05 19:01 | 1612 | ENOI | XFMR | 74855 | 43917492046 | DLIN | 6 | 1 | 335 | 335 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to replace transformer in 3 pot bank. | -89.9458 | 30.0127 | 70129 | E | Council District E | Kristin Palmer
1302625046 | Yes | EAST ORLEANS | COLD | 2019-01-23 14:15 | 2019-01-23 14:15 | 2019-01-23 19:00 | 1002 | ENOI | XFMR | 51972 | 41534489926 | DLIN | 6 | 2 | 570 | 285 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad transformer | -90.0211 | 30.0076 | 70126 | E | Council District E | Kristin Palmer
1302555673 | Yes | EAST ORLEANS | FAIR | 2019-01-22 13:18 | 2019-01-22 13:18 | 2019-01-22 13:44 | 2223 | ENOI | XFMR | 1487065 | 43261508965 | DLIN | 6 | 3 | 78 | 26 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -89.9659 | 30.0594 | 70128 | E | Council District E | Jared Brossett
1300757954 | Yes | EAST ORLEANS | FAIR | 2018-12-08 17:18 | 2018-12-08 21:18 | 2018-12-08 23:01 | 2212 | ENOI | XFMR | 80178 | 42011499434 | DLIN | 6 | 4 | 1372 | 343 | EQUIPMENT | ETRD | Equipment - Transformer | N | replaced transformer | -90.0057 | 30.0336 | 70126 | E | Council District E | Jared Brossett
1301924619 | Yes | ORLEANS | FAIR | 2018-12-31 16:42 | 2018-12-31 16:42 | 2019-01-01 01:24 | 1923 | ENOI | XFMR | 64453 | 39255459757 | DLIN | 1 | 4 | 2088 | 522 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.0942 | 29.9253 | 70115 | B | Council District B | Jared Brossett
1302541832 | Yes | ORLEANS | FAIR | 2019-01-22 03:14 | 2019-01-22 03:14 | 2019-01-22 08:31 | 2024 | ENOI | XFMR | 78710 | 38503464688 | DLIN | 1 | 6 | 1896 | 316 | EQUIPMENT | ETRD | Equipment - Transformer | N | Equipment - Transformer | -90.1177 | 29.9392 | 70118 | A | Council District A | Kristin Palmer
1302628846 | Yes | EAST ORLEANS | COLD | 2019-01-23 16:29 | 2019-01-23 19:20 | 2019-01-23 23:23 | 508 | ENOI | XFMR | 7230 | 41072492970 | DLIN | 6 | 6 | 2484 | 414 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.0356 | 30.0161 | 70126 | D | Council District D | Cyndi Nguyen
1300651624 | Yes | ORLEANS | FAIR | 2018-12-05 17:51 | 2018-12-05 17:51 | 2018-12-05 18:02 | 2026 | ENOI | XFMR | 68438 | 38678477387 | DLIN | 1 | 8 | 88 | 11 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew changed bad transformer | -90.1118 | 29.9741 | 70118 | A | Council District A | Kristin Palmer
1302502172 | Yes | ORLEANS | FAIR | 2019-01-20 09:54 | 2019-01-20 10:31 | 2019-01-20 12:20 | 1704 | ENOI | XFMR | 548532 | 39836488077 | DLIN | 1 | 8 | 1168 | 146 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot, crew changed out | -90.0749 | 30.003 | 70122 | D | Council District D | Jared Brossett
1302824514 | Yes | ORLEANS | FAIR | 2019-01-30 14:21 | 2019-01-30 14:24 | 2019-01-30 16:55 | 1709 | ENOI | XFMR | 54945 | 40047480904 | DLIN | 1 | 8 | 1232 | 154 | EQUIPMENT | ETRD | Equipment - Transformer | N | Equipment - Transformer | -90.0685 | 29.9832 | 70119 | D | Council District D | Kristin Palmer
1302800300 | Yes | EAST ORLEANS | COLD | 2019-01-29 19:12 | 2019-01-29 19:57 | 2019-01-29 22:39 | 1607 | ENOI | XFMR | 32206 | 42348493412 | DLIN | 6 | 8 | 1648 | 206 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to change UG transformer | -89.9952 | 30.0169 | 70126 | E | Council District E | Jared Brossett
1300915950 | Yes | EAST ORLEANS | COLD | 2018-12-11 20:32 | 2018-12-11 22:45 | 2018-12-12 00:31 | 2212 | ENOI | XFMR | 77045 | 42073501110 | DLIN | 6 | 8 | 1904 | 238 | EQUIPMENT | ETRD | Equipment - Transformer | N | Equipment - Transformer ( OPEN IN V24 CLOSED N/OPEN IN V30 | -90.0037 | 30.0382 | 70126 | E | Council District E | Joseph Giarrusso
1301776353 | Yes | EAST ORLEANS | FAIR | 2018-12-28 07:53 | 2018-12-28 12:08 | 2018-12-28 14:35 | 508 | ENOI | XFMR | 51680 | 40818493701 | DLIN | 6 | 8 | 3216 | 402 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad transformer | -90.0436 | 30.0182 | 70126 | D | Council District D | Cyndi Nguyen
1300652399 | Yes | EAST ORLEANS | FAIR | 2018-12-05 19:11 | 2018-12-05 19:20 | 2018-12-05 22:10 | 622 | ENOI | XFMR | 77994 | 40870478454 | DLIN | 6 | 9 | 1611 | 179 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew chnaged bad transformer | -90.0426 | 29.9762 | 70117 | D | Council District D | Cyndi Nguyen
1302187745 | Yes | ORLEANS | FAIR | 2019-01-12 14:16 | 2019-01-12 16:55 | 2019-01-12 18:21 | 2016 | ENOI | XFMR | 65761 | 38308472895 | DLIN | 1 | 9 | 2205 | 245 | EQUIPMENT | ETRD | Equipment - Transformer | N | Equipment - Transformer, crew changed out | -90.1237 | 29.9618 | 70118 | A | Council District A | Kristin Palmer
1301661678 | Yes | ORLEANS | THDR | 2018-12-27 08:45 | 2018-12-27 13:25 | 2018-12-27 16:01 | 2132 | ENOI | XFMR | 1000492 | 39724460874 | DLIN | 1 | 10 | 4360 | 436 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew replaced transdformer | -90.0794 | 29.9282 | 70130 | B | Council District B | Jared Brossett
1300600136 | Yes | ORLEANS | FAIR | 2018-12-03 16:41 | 2018-12-03 22:43 | 2018-12-03 23:05 | 1917 | ENOI | XFMR | 78752 | 38994459054 | DLIN | 1 | 12 | 4608 | 384 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.1025 | 29.9236 | 70115 | B | Council District B | Cyndi Nguyen
1302245434 | Yes | EAST ORLEANS | FAIR | 2019-01-15 17:59 | 2019-01-15 18:26 | 2019-01-15 19:30 | 613 | ENOI | LFUS | 42889 | 4046247935 | DLIN | 6 | 13 | 1183 | 91 | EQUIPMENT | ETRD | Equipment - Transformer | N | bushings burned up on transformer crew to replace | -90.0553 | 29.9788 | 70117 | D | Council District D | Joseph Giarrusso
1301491706 | Yes | ORLEANS | FAIR | 2018-12-24 06:51 | 2018-12-24 08:47 | 2018-12-24 10:06 | B0527 | ENOI | XFMR | 498755 | 38279471547 | DLIN | 1 | 14 | 2730 | 195 | EQUIPMENT | ETRD | Equipment - Transformer | N | Crew is on site replacing bad transformer | -90.1246 | 29.9581 | 70118 | A | Council District A | Joseph Giarrusso
1302499579 | Yes | ORLEANS | WIND | 2019-01-20 08:07 | 2019-01-20 11:56 | 2019-01-20 13:41 | 2014 | ENOI | XFMR | 59904 | 37952469662 | DLIN | 1 | 15 | 5010 | 334 | EQUIPMENT | ETRD | Equipment - Transformer | N | bad pot | -90.135 | 29.9529 | 70118 | A | Council District A | Cyndi Nguyen
1301435605 | Yes | EAST ORLEANS | FAIR | 2018-12-21 05:54 | 2018-12-21 07:49 | 2018-12-21 13:03 | 1010 | ENOI | LFUS | 14933-F | 4140249868 | DLIN | 6 | 15 | 6435 | 429 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.0249 | 30.0316 | 70126 | D | Council District D | Jay Banks
1301419828 | Yes | ALGIERS | THDR | 2018-12-20 19:27 | 2018-12-20 19:27 | 2018-12-20 20:29 | W0725 | ENOI | LFUS | 33897 | 4154346243 | DLIN | 81 | 16 | 976 | 61 | EQUIPMENT | ETRD | Equipment - Transformer | N | changed padmount transformer | -90.0219 | 29.932 | 70114 | C | Council District C | Joseph Giarrusso
1302057685 | Yes | ORLEANS | FAIR | 2019-01-06 14:58 | 2019-01-06 14:58 | 2019-01-06 19:01 | 911 | ENOI | XFMR | 1571585 | 39114477522 | DLIN | 1 | 16 | 3888 | 243 | EQUIPMENT | ETRD | Equipment - Transformer | N | change bad pot | -90.098 | 29.9743 | 70119 | A | Council District A | Cyndi Nguyen
1301445500 | Yes | ORLEANS | FAIR | 2018-12-21 12:58 | 2018-12-21 13:23 | 2018-12-21 14:45 | 2027 | ENOI | XFMR | 28987 | 38618472008 | DLIN | 1 | 17 | 1802 | 106 | EQUIPMENT | ETRD | Equipment - Transformer | N | LEAKING TRANSFORMER CREW TO REPLACE | -90.1139 | 29.9593 | 70125 | B | Council District B | Cyndi Nguyen
1300603945 | Yes | ORLEANS | FAIR | 2018-12-03 22:42 | 2018-12-04 00:13 | 2018-12-04 02:18 | 2027 | ENOI | XFMR | 28601 | 38684471019 | DLIN | 1 | 21 | 4536 | 216 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.1119 | 29.9565 | 70125 | B | Council District B | Jay Banks
1301774318 | Yes | ORLEANS | THDR | 2018-12-28 05:42 | 2018-12-28 07:55 | 2018-12-28 10:05 | 409 | ENOI | XFMR | 19811 | 38443491194 | DLIN | 1 | 21 | 5523 | 263 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew changed out bad trans | -90.1188 | 30.0121 | 70124 | A | Council District A | Joseph Giarrusso
1302800260 | Yes | ORLEANS | COLD | 2019-01-29 19:08 | 2019-01-29 23:14 | 2019-01-29 23:42 | 1912 | ENOI | XFMR | 531758 | 3835645638 | DLIN | 1 | 23 | 6302 | 274 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to change transformer | -90.1227 | 29.9163 | 70115 | A | Council District A | Kristin Palmer
1301411775 | Yes | ALGIERS | THDR | 2018-12-20 16:56 | 2018-12-20 17:18 | 2018-12-20 20:28 | W0725 | ENOI | XFMR | BY115718 | 4157546243 | DLIN | 81 | 29 | 6148 | 212 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew to replace xfmr | -90.0209 | 29.932 | 70114 | C | Council District C | Joseph Giarrusso
1302685606 | Yes | EAST ORLEANS | FAIR | 2019-01-25 21:50 | 2019-01-25 21:50 | 2019-01-26 00:06 | 2223 | ENOI | LFUS | 27108 | 4397251427 | DLIN | 6 | 35 | 4760 | 136 | EQUIPMENT | ETRD | Equipment - Transformer | N | Padmount transformer failed. Crew changed out and power is back to normal. | -89.9432 | 30.0738 | 70128 | E | Council District E | Jared Brossett
1300820397 | Yes | EAST ORLEANS | COLD | 2018-12-09 09:38 | 2018-12-09 11:29 | 2018-12-09 11:26 | 1205 | ENOI | LFUS | 25848 | 4438450346 | DLIN | 6 | 39 | 4212 | 108 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew changed bad pad | -97.0758 | 27.9066 | 70129 | E | Council District E | Jared Brossett
1302713526 | Yes | EAST ORLEANS | FAIR | 2019-01-28 01:09 | 2019-01-28 03:45 | 2019-01-28 05:01 | 2223 | ENOI | LFUS | 27108 | 4397251427 | DLIN | 6 | 48 | 11088 | 231 | EQUIPMENT | ETRD | Equipment - Transformer | N | Crewreplaced back transformer | -89.9432 | 30.0738 | 70128 | E | Council District E | Kristin Palmer
1302688666 | Yes | ORLEANS | FAIR | 2019-01-26 07:35 | 2019-01-26 11:04 | 2019-01-26 13:31 | 907 | ENOI | XFMR | 1413671 | 3986247585 | DLIN | 1 | 52 | 18512 | 356 | EQUIPMENT | ETRD | Equipment - Transformer | N |  | -90.0745 | 29.9694 | 70116 | D | Council District D | Jared Brossett
1300915420 | Yes | EAST ORLEANS | FAIR | 2018-12-11 20:32 | 2018-12-11 21:27 | 2018-12-11 22:15 | 2212 | ENOI | LFUS | 24971 | 4214250165 | DLIN | 6 | 60 | 6180 | 103 | EQUIPMENT | ETRD | Equipment - Transformer | N | Equipment - Transformer V23 IS BAD AND TOOK OUT POLE DIP L24971 | -90.0015 | 30.0396 | 70126 | E | Council District E | Jay Banks
1300674774 | Yes | EAST ORLEANS | FAIR | 2018-12-06 17:00 | 2018-12-06 20:20 | 2018-12-07 00:30 | 1205 | ENOI | XFMR | 32814 | 44959501841 | DLIN | 6 | 159 | 71550 | 450 | EQUIPMENT | ETRD | Equipment - Transformer | N | crew changed bad transformer | -89.9125 | 30.0392 | 70129 | E | Council District E | Jared Brossett
1302187113 | Yes | ORLEANS | FAIR | 2019-01-12 14:16 | 2019-01-12 15:07 | 2019-01-12 15:10 | 2016 | ENOI | LFUS | 33243 | 3832347263 | DLIN | 1 | 172 | 9288 | 54 | EQUIPMENT | ETRD | Equipment - Transformer | N | transformer failed and took out line, refused ok crew will change trans | -90.1232 | 29.9609 | 70118 | A | Council District A | Kristin Palmer
1301439930 | Yes | EAST ORLEANS | FAIR | 2018-12-21 09:59 | 2018-12-21 09:59 | 2018-12-21 14:02 | 616 | ENOI | LFUS | 21876 | 4132848611 | DLIN | 6 | 4 | 972 | 243 | OTHER | FOTH | Fire - Other (Describe in Remarks Field) | N | POLE AT LOCATON CAUGHT FIRE HAD TO TAKE OUT LATERAL 21876 FOR CREW TO DO WORK | -90.0275 | 29.9975 | 70126 | D | Council District D | Cyndi Nguyen
1300566759 | Yes | ALGIERS | FOGG | 2018-12-01 20:15 | 2018-12-01 20:15 | 2018-12-01 22:29 | W1715 | ENOI | TFUS | 1320625 | 4449545715 | DLIN | 81 | 1 | 134 | 134 | OTHER | UNKN | Inspected Unknown | N | back n now lat was blown at delercrox brizzut | -89.9289 | 29.9165 | 70131 | C | Council District C | Joseph Giarrusso
1300565833 | Yes | ALGIERS | FAIR | 2018-12-01 19:02 | 2018-12-01 19:02 | 2018-12-01 21:31 | W0112 | ENOI | TFUS | C72293 | 4081546633 | DLIN | 81 | 1 | 149 | 149 | OTHER | UNKN | Inspected Unknown | N | back n now brizzut | -90.0447 | 29.943 | 70114 | C | Council District C | Jared Brossett
1301335678 | Yes | EAST ORLEANS | FAIR | 2018-12-19 06:58 | 2018-12-19 06:58 | 2018-12-19 09:33 | 1202 | ENOI | LFUS | 95206 | 4528949541 | DLIN | 6 | 1 | 155 | 155 | OTHER | UNKN | Inspected Unknown | N | Changed **TFUS 1486537 1 to LFUS 1486537 1** --- Refused A and B phase at lateral sw# 95206 feeding padmount transformer jvickna | -89.9023 | 30.0214 | 70129 | E | Council District E | Joseph Giarrusso
1302197309 | Yes | ORLEANS | FAIR | 2019-01-13 11:13 | 2019-01-13 11:13 | 2019-01-13 11:42 | 2014 | ENOI | TFUS | C44259 | 38289465129 | DLIN | 1 | 4 | 116 | 29 | OTHER | UNKN | Inspected Unknown | N |  | -90.1245 | 29.9404 | 70118 | A | Council District A | Joseph Giarrusso
1302243383 | Yes | ALGIERS | FAIR | 2019-01-15 15:41 | 2019-01-15 15:41 | 2019-01-15 17:46 | W0112 | ENOI | TFUS | BY158080 | 4075546515 | DLIN | 81 | 4 | 500 | 125 | OTHER | UNKN | Inspected Unknown | N | back on brizzut | -90.0466 | 29.9397 | 70114 | C | Council District C | Jay Banks
1302035783 | Yes | ALGIERS | FAIR | 2019-01-04 17:23 | 2019-01-04 17:39 | 2019-01-04 18:47 | W0715 | ENOI | TFUS | 1042742 | 4132645902 | DLIN | 81 | 5 | 420 | 84 | OTHER | UNKN | Inspected Unknown | N | back on brizzut | -90.0288 | 29.9226 | 70114 | C | Council District C | Cyndi Nguyen
1300987799 | Yes | EAST ORLEANS | FAIR | 2018-12-14 07:13 | 2018-12-14 07:13 | 2018-12-14 07:56 | 1604 | ENOI | TFUS | 65670 | 42759494914 | DLIN | 6 | 6 | 252 | 42 | OTHER | UNKN | Inspected Unknown | N | blown transformer fuse-refused transformer ok-custs back on-voltage ok swalsh1 12-14-18 swalsh1 | -89.9823 | 30.0209 | 70127 | E | Council District E | Joseph Giarrusso
1302699373 | Yes | ALGIERS | FAIR | 2019-01-27 04:27 | 2019-01-27 04:32 | 2019-01-27 05:24 | W0712 | ENOI | TFUS | BY75278 | 4202545785 | DLIN | 81 | 10 | 570 | 57 | OTHER | UNKN | Inspected Unknown | N | back n now found nothing feuse was blown brizzut | -90.0068 | 29.9193 | 70131 | C | Council District C | Joseph Giarrusso
1301433843 | Yes | EAST ORLEANS | WIND | 2018-12-21 00:53 | 2018-12-21 02:57 | 2018-12-21 04:00 | 502 | ENOI | LFUS | 61200 | 4062249108 | DLIN | 6 | 10 | 1870 | 187 | OTHER | UNKN | Inspected Unknown | N | B phase blown at sw 61200 taken ouy by weather refused ok dfahr | -90.0499 | 30.011 | 70122 | D | Council District D | Kristin Palmer
1302035902 | Yes | ALGIERS | FAIR | 2019-01-04 17:29 | 2019-01-04 17:32 | 2019-01-04 18:46 | W0715 | ENOI | TFUS | BY9-2143 | 4129345912 | DLIN | 81 | 12 | 924 | 77 | OTHER | UNKN | Inspected Unknown | N | back on brizzut | -90.0299 | 29.923 | 70114 | C | Council District C | Kristin Palmer
1301612941 | Yes | ORLEANS | THDR | 2018-12-27 02:47 | 2018-12-27 02:55 | 2018-12-27 03:31 | 509 | ENOI | LFUS | 17884 | 3964049269 | DLIN | 1 | 17 | 748 | 44 | OTHER | UNKN | Inspected Unknown | N | wind blew phases into tree refused ok tsmit29 | -90.0808 | 30.0157 | 70122 | D | Council District D | Kristin Palmer
1302726409 | Yes | EAST ORLEANS | FAIR | 2019-01-28 13:50 | 2019-01-28 13:50 | 2019-01-28 15:46 | 614 | ENOI | TFUS | 70952 | 40446474553 | DLIN | 6 | 19 | 2204 | 116 | OTHER | UNKN | Inspected Unknown | N | refused blown transformer. found no sign of anything taking it out. all customers back on. dmorehe dmorehe | -90.0561 | 29.9656 | 70117 | C | Council District C | Joseph Giarrusso
1301436840 | Yes | ORLEANS | COLD | 2018-12-21 07:41 | 2018-12-21 08:19 | 2018-12-21 09:57 | 2011 | ENOI | LFUS | 64697 | 39372479437 | DLIN | 1 | 21 | 2856 | 136 | OTHER | UNKN | Inspected Unknown | N | Changed **TFUS 64697 21 to LFUS 64697 21** --- refused b phase. per 310 treed3 | -90.0899 | 29.9794 | 70119 | A | Council District A | Jared Brossett
1301272559 | Yes | ALGIERS | FAIR | 2018-12-17 16:09 | 2018-12-17 17:15 | 2018-12-17 17:48 | W1714 | ENOI | LFUS | 5602 | 4249645530 | DLIN | 81 | 28 | 2772 | 99 | OTHER | UNKN | Inspected Unknown | N | back on brizzut | -89.9919 | 29.9121 | 70131 | C | Council District C | Joseph Giarrusso
1302696130 | Yes | ORLEANS | FAIR | 2019-01-26 17:15 | 2019-01-26 17:16 | 2019-01-26 17:34 | 407 | ENOI | LFUS | 17710 | 3867749021 | DLIN | 1 | 35 | 665 | 19 | OTHER | UNKN | Inspected Unknown | N | refused lateral tsmit29 | -90.1115 | 30.0092 | 70124 | A | Council District A | Jared Brossett
1302194118 | Yes | EAST ORLEANS | FAIR | 2019-01-13 07:25 | 2019-01-13 07:40 | 2019-01-13 08:25 | 1702 | ENOI | LFUS | 21625 | 4057148946 | DLIN | 6 | 35 | 2100 | 60 | OTHER | UNKN | Inspected Unknown | N | found A phase blown refused ok dfahr | -90.0515 | 30.0066 | 70122 | D | Council District D | Kristin Palmer
1302637266 | Yes | EAST ORLEANS | FAIR | 2019-01-23 22:09 | 2019-01-23 22:52 | 2019-01-23 23:36 | 1611 | ENOI | LFUS | 21769 | 4296949346 | DLIN | 6 | 52 | 4524 | 87 | OTHER | UNKN | Inspected Unknown | N | refused b phase/ high wind.. tbrock | -89.9756 | 30.0168 | 70127 | E | Council District E | Cyndi Nguyen
1301475195 | Yes | EAST ORLEANS | FAIR | 2018-12-22 22:50 | 2018-12-23 00:12 | 2018-12-23 00:52 | 2214 | ENOI | LFUS | 25878 | 4309450396 | DLIN | 6 | 54 | 6588 | 122 | OTHER | UNKN | Inspected Unknown | N | refused A phase in cub 61 sw25878 refused ok rode out all transformers in dfahr | -97.0758 | 27.9066 | 70128 | E | Council District E | Jared Brossett
1302620166 | Yes | ORLEANS | THDR | 2019-01-23 11:21 | 2019-01-23 12:56 | 2019-01-23 12:59 | 510 | ENOI | LFUS | 34386 | 3994649489 | DLIN | 1 | 158 | 15484 | 98 | OTHER | UNKN | Inspected Unknown | N | refused B phase cause unkown jbologn | -90.0712 | 30.0217 | 70122 | D | Council District D | Kristin Palmer
1302197647 | Yes | ORLEANS | COLD | 2019-01-13 12:03 | 2019-01-13 12:05 | 2019-01-13 13:27 | 2014 | ENOI | LFUS | 56819 | 3829546523 | DLIN | 1 | 1 | 84 | 84 | OVERLOAD | OVLD | Overload | N | overloaded due to cold. refused b phase. 1 transformer on it feeding location. abengst | -90.1243 | 29.9405 | 70118 | A | Council District A | Cyndi Nguyen
1301939669 | NO | ORLEANS | RAIN | 2019-01-01 08:26 | 2019-01-01 08:26 | 2019-01-01 11:05 | 2013 | ENOI | SERV | SERVICE | 38165468768 | DLIN | 1 | 1 | 0 | 0 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 526980 20 to ERR 526980 1** --- repaired bad connection in service dsmit36 | -90.1282 | 29.9503 | 70118 | A | Council District A | Kristin Palmer
1302480366 | Yes | ORLEANS | WIND | 2019-01-19 20:32 | 2019-01-19 20:32 | 2019-01-19 20:40 | 615 | ENOI | SECO | SECONDARY | 39914479704 | DLIN | 1 | 1 | 7 | 7 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | secondary jumper came loose at kearny jcox7 | -90.0726 | 29.98 | 70119 | D | Council District D | Joseph Giarrusso
1301756961 | Yes | ORLEANS | WIND | 2018-12-27 17:52 | 2018-12-27 17:52 | 2018-12-27 18:10 | 2016 | ENOI | SECO | SECONDARY | 38582469145 | DLIN | 1 | 1 | 18 | 18 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | repaired 4/0 secondaries in rear at location | -90.1151 | 29.9513 | 70125 | A | Council District A | Cyndi Nguyen
1301952560 | Yes | ORLEANS | FAIR | 2019-01-01 14:38 | 2019-01-01 14:43 | 2019-01-01 16:01 | 2147 | ENOI | SERV | SERVICE | 39646458784 | DLIN | 1 | 1 | 83 | 83 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 63849 13 to SERV 63849 1** --- repaired bad service dsmit36 | -90.0818 | 29.9226 | 70115 | B | Council District B | Jared Brossett
1302155430 | Yes | ORLEANS | COLD | 2019-01-10 19:24 | 2019-01-10 19:24 | 2019-01-10 21:06 | 627 | ENOI | SECO | SECONDARY | 40171482985 | DLIN | 1 | 1 | 102 | 102 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 60273 * 8 to SECO 60273 * [count]** --- repaired burned sec wire. dsmit36 | -90.0644 | 29.9889 | 70122 | D | Council District D | Joseph Giarrusso
1300653402 | Yes | EAST ORLEANS | FAIR | 2018-12-05 21:03 | 2018-12-05 21:08 | 2018-12-05 22:55 | 1709 | ENOI | SERV | 56820 | 40368484132 | DLIN | 6 | 1 | 112 | 112 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 56820 5 to TFUS 56820 2** --- Installed new 1/0 service to location jvickna | -90.0582 | 29.992 | 70122 | D | Council District D | Jared Brossett
1302654514 | Yes | ORLEANS | FAIR | 2019-01-24 13:05 | 2019-01-24 13:05 | 2019-01-24 15:21 | 400 | ENOI | LFUS | SECONDARY | 3831747940 | DLIN | 1 | 1 | 136 | 136 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | repaired underground secondary | -90.1231 | 29.9796 | 70124 | A | Council District A | Jared Brossett
1301454174 | Yes | EAST ORLEANS | FAIR | 2018-12-21 20:51 | 2018-12-21 20:51 | 2018-12-21 23:21 | 623 | ENOI | SERV | 1473712 | 40447475208 | DLIN | 6 | 1 | 150 | 150 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 1473712 19 to SERV 1473712 19** --- service burnt/ changed to 1/0.. tbrock | -90.056 | 29.9675 | 70117 | C | Council District C | Joseph Giarrusso
1300958888 | Yes | EAST ORLEANS | THDR | 2018-12-13 11:27 | 2018-12-13 11:27 | 2018-12-13 14:00 | 2215 | ENOI | SERV | 1541054 | 43238507611 | DLIN | 6 | 1 | 153 | 153 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | contract crew to install drycell | -89.9666 | 30.0556 | 70128 | E | Council District E | Joseph Giarrusso
1302714758 | Yes | ORLEANS | COLD | 2019-01-28 07:14 | 2019-01-28 07:14 | 2019-01-28 09:47 | 1709 | ENOI | SERV | SERVICE | 39597482096 | DLIN | 1 | 1 | 153 | 153 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 57059 5 to SERV 57059 1** --- replaced service wire dsmit36 | -90.0826 | 29.9867 | 70119 | A | Council District A | Kristin Palmer
1301041744 | Yes | ORLEANS CBD | FAIR | 2018-12-15 11:04 | 2018-12-15 11:04 | 2018-12-15 13:50 | COMMO | ENOI | NTWK | 1 | 3990347014 | DLIN | 4 | 1 | 166 | 166 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | repaired burned up cable in man hole |  |  | 70122 | B | Council District B | Jay Banks
1302845809 | Yes | EAST ORLEANS | FAIR | 2019-01-31 17:10 | 2019-01-31 17:10 | 2019-01-31 20:20 | 2213 | ENOI | SERV | SERVICE | 44563509746 | DLIN | 6 | 1 | 190 | 190 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Crew installed Drycell at location. | -89.9246 | 30.0611 | 70129 | E | Council District E | Jay Banks
1301672746 | Yes | ORLEANS | WIND | 2018-12-27 09:47 | 2018-12-27 09:47 | 2018-12-27 13:17 | 1708 | ENOI | SERV | 63076 | 40158484463 | DLIN | 1 | 1 | 210 | 210 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 63076 12 to TFUS 63076 1** --- service burned up at wilson rack. changed out service and checked voltage jcox7 | -90.0647 | 29.993 | 70122 | D | Council District D | Jay Banks
1302522036 | Yes | EAST ORLEANS | FAIR | 2019-01-21 08:24 | 2019-01-21 08:24 | 2019-01-21 12:16 | 1603 | ENOI | SECO | SECONDARY | 42567501187 | DLIN | 6 | 1 | 232 | 232 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Svc burned up in panel... 1107.. 1/21/19 rbeaco crew repaired burned up secondary UG | -89.988 | 30.0382 | 70127 | E | Council District E | Joseph Giarrusso
1302040872 | Yes | EAST ORLEANS | FAIR | 2019-01-05 07:42 | 2019-01-05 07:42 | 2019-01-05 12:30 | 1607 | ENOI | SERV | SERVICE | 42029493934 | DLIN | 6 | 1 | 288 | 288 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | repair bad underground cable | -90.0053 | 30.0185 | 70126 | E | Council District E | Kristin Palmer
1301690335 | NO | ORLEANS | THDR | 2018-12-27 11:11 | 2018-12-27 14:19 | 2018-12-27 17:51 |  | N/A | SERV | SERVICE COND | 00000000000 | DLIN | 1 | 1 | 400 | 400 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | repaired leg on service |  |  | #N/A | #N/A | #N/A | Joseph Giarrusso
1300932171 | Yes | ORLEANS | FAIR | 2018-12-12 09:59 | 2018-12-12 13:58 | 2018-12-12 16:00 | 1912 | ENOI | SERV | SERVICE | 38929456810 | DLIN | 1 | 3 | 1083 | 361 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS 1370945 * 16 to SERV 1370945 * 16** --- Replaced secondary service connection at transformer feeding wilson rack jvickna | -90.1047 | 29.9173 | 70115 | B | Council District B | Cyndi Nguyen
1300623282 | Yes | EAST ORLEANS | FAIR | 2018-12-04 16:25 | 2018-12-04 20:06 | 2018-12-04 21:51 | 2217 | ENOI | TFUS | 69904 | 43663509105 | DLIN | 6 | 4 | 1304 | 326 | CONDUCTOR | ESEC | Secondary/Service Conductor | N |  | -89.9532 | 30.0596 | 70128 | E | Council District E | Cyndi Nguyen
1300833956 | Yes | EAST ORLEANS | FAIR | 2018-12-09 13:02 | 2018-12-09 13:53 | 2018-12-09 18:01 | 1204 | ENOI | TFUS | 1314066 | 48007512587 | DLIN | 6 | 7 | 2093 | 299 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | bad main line secondary | -89.8156 | 30.0677 | 70129 | E | Council District E | Cyndi Nguyen
1300706412 | Yes | EAST ORLEANS | FAIR | 2018-12-07 23:52 | 2018-12-08 02:18 | 2018-12-08 03:51 | 1607 | ENOI | TFUS | 68281 | 42204493255 | DLIN | 6 | 9 | 2142 | 238 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | 2 SPANS SECONDARY REPAIRED | -89.9999 | 30.0165 | 70126 | E | Council District E | Joseph Giarrusso
1300666828 | NO | ALGIERS | FAIR | 2018-12-06 13:38 | 2018-12-06 14:05 | 2018-12-06 20:00 | W0113 | ELA | TFUS | 1204926 | 4092546267 | DLIN | 81 | 14 | 5348 | 382 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | bad ug cable, repaired | -90.0414 | 29.9328 | 70114 | C | Council District C | Joseph Giarrusso
1302248883 | Yes | EAST ORLEANS | FAIR | 2019-01-16 05:13 | 2019-01-16 06:44 | 2019-01-16 07:12 | 501 | ENOI | TFUS | 1395398 | 40892492073 | DLIN | 6 | 22 | 2618 | 119 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | open wire secondary burned down, made repairs and re energized | -90.0413 | 30.0136 | 70126 | D | Council District D | Kristin Palmer
1302503659 | Yes | ALGIERS | THDR | 2019-01-20 10:57 | 2019-01-20 11:00 | 2019-01-20 11:18 | W1714 | ENOI | LFUS | 5632 | 4262445642 | DLIN | 81 | 32 | 672 | 21 | CONDUCTOR | ESEC | Secondary/Service Conductor | N | Changed **TFUS BY9-7335 19 to LFUS BY9-7335 1** --- wind blew open wire together/ untangled and refused lateral #5632 nwashi1 | -89.9879 | 29.9151 | 70131 | C | Council District C | Jared Brossett
1302516027 | Yes | ORLEANS | COLD | 2019-01-21 00:32 | 2019-01-21 00:32 | 2019-01-21 02:18 | 510 | ENOI | TFUS | 33509 | 39888493267 | DLIN | 1 | 7 | 742 | 106 | CONDUCTOR | SLAK | Slack Conductor / Inadequate Phase Spacing | N | repaired (b) phase jumper, came out of switch jcox7 | -90.0731 | 30.0173 | 70122 | D | Council District D | Joseph Giarrusso
1302468449 | Yes | ORLEANS | WIND | 2019-01-19 18:13 | 2019-01-19 19:55 | 2019-01-19 19:55 | 512 | ENOI | LFUS | 17538 | 4012149001 | DLIN | 1 | 52 | 5304 | 102 | CONDUCTOR | SLAK | Slack Conductor / Inadequate Phase Spacing | N | Changed **LFUS 17538 171 to LFUS 17538 52** --- refused c phase jcox7 | -90.0659 | 30.0083 | 70122 | D | Council District D | Joseph Giarrusso
1302491622 | Yes | ORLEANS | WIND | 2019-01-20 00:19 | 2019-01-20 00:53 | 2019-01-20 01:11 | 911 | ENOI | LFUS | 21551 | 3912247801 | DLIN | 1 | 80 | 4160 | 52 | CONDUCTOR | SLAK | Slack Conductor / Inadequate Phase Spacing | N | took slack out sheild and re fused jcox7 | -90.0979 | 29.9756 | 70119 | A | Council District A | Cyndi Nguyen
1300915019 | Yes | EAST ORLEANS | FAIR | 2018-12-11 20:33 | 2018-12-11 21:05 | 2018-12-11 21:15 | 2212 | ENOI | LFUS | 27648 | 4212050212 | DLIN | 6 | 47 | 1974 | 42 | OTHER | UNKI | Unknown - Under Investigation | N | l/fuse l24971 blow and went back to l/fuse l 27648 | -90.0021 | 30.041 | 70126 | E | Council District E | Joseph Giarrusso
1302425572 | Yes | EAST ORLEANS | WIND | 2019-01-19 13:41 | 2019-01-19 17:33 | 2019-01-19 18:31 | 2214 | ENOI | LFUS | 25603 | 4335450503 | DLIN | 6 | 69 | 20010 | 290 | OTHER | UNKI | Unknown - Under Investigation | N |  | -97.0758 | 27.9066 | 70128 | E | Council District E | Jared Brossett
1301602165 | NO | EAST ORLEANS | THDR | 2018-12-27 01:45 | 2018-12-27 01:45 | 2018-12-27 01:46 | 513 | ENOI | SBKR | 513 | 4074749223 | DLIN | 6 | 99 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N | weather moving through area | -90.046 | 30.0142 | 70126 | D | Council District D | Jared Brossett
1301350187 | NO | ORLEANS | FAIR | 2018-12-19 12:10 | 2018-12-19 12:10 | 2018-12-19 12:10 | 400 | ENOI | SBKR | 400 | 3847049127 | DLIN | 1 | 309 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N | S&WB FEEDER,TO BE PATROLLED | -90.1179 | 30.0122 | 70124 | A | Council District A | Kristin Palmer
1301437166 | NO | EAST ORLEANS | FAIR | 2018-12-21 07:57 | 2018-12-21 07:57 | 2018-12-21 07:57 | 506 | ENOI | SBKR | 506 | 4074749220 | DLIN | 6 | 1146 | 0 | 0 | OTHER | UNKI | Unknown - Under Investigation | N |  | -90.0459 | 30.0141 | 70126 | D | Council District D | Cyndi Nguyen